## General Su...- CAYUGA 230 KV-52
General Summary Report
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | Case 3 Duct Bank 3 ft 2 ft sep
Date: |  | 1/8/2026 12:34:43 PM
Simulation Data
Installation type: |  | Multiple Ductbanks
Steady State Option |  | Temperature
Ambient temperature [°C] |  | 29
Native Soil Thermal Resistivity [K.m/W] |  | 0.9
Consider Non-Isothermal Earth Surface |  | No
Consider effect of soil dry out |  | No
Consider Electrical interaction between circuits |  | No
Induced current in metallic layers as a fraction of conductor current (applied to all single phase circuits) [A] |  | 0
Installation Type:Multiple Ductbanks/Backfills
Ambient Soil Temperature at Installation Depth [°C] |  | 29
Native Soil Thermal Resistivity [K.m/W] |  | 0.9
Consider Non-Isothermal Earth Surface |  | No
Layer Name |  | X [ft] | Y [ft] | Width [ft] | Height [ft] | Thermal Resistivity [K.m/W]
NSTD DB1 |  | -1.755 | 3.75 | 3.5 | 1.5 | 0.6
Sub Base |  | 0 | 1 | 7 | 0.99 | 2.5
Gravel Bed |  | 0 | 4.75 | 7 | 0.5 | 2.5
NSTD DB2 |  | 1.755 | 3.75 | 3.5 | 1.5 | 0.6
FTB R |  | 0 | 2.2475 | 7 | 1.505 | 1
Asphalt |  | 0 | 0.2525 | 7 | 0.505 | 3.5
General Cable Information
Cable ID |  | Number of Cores | Conductor Construction | Voltage [kV] | Conductor Area [mm²] | Cable Overall Diameter [in] | Maximum Steady-State Conductor Temperature [ºC] | Maximum Emergency Conductor Temperature [ºC]
CAYUGA 230KV 5000 KCMIL |  | Single Core | 6 Segments | 230 | 2535.636 | 5.4595 | 90 | 110
Detailed Cable Information
Cable ID |  | Conductor | Insulation | Sheath / Tape | Concentric Wires | Filler | Armour | Jacket / Armour Serving
CAYUGA 230KV 5000 KCMIL |  | Copper | XLPE Unfilled | Copper | Copper | n/a | n/a | Polyethylene
General Input Data
Cable | Cable ID | Circuit No. | Phase | Fq [Hz] | X [ft] | Y [ft] | DLF [p.u.] | Sheath / Shield Bonding
Cable Index Number | Cable Equipment ID | Circuit No. | Cable Phase | Operating Frequency | X coordinate | Y coordinate | Daily Load Factor | Bonding Type
1 | CAYUGA 230KV 5000 KCMIL | 1 | A | 60 | -2.755 | 3.9143 | 1 | Multicables 1 Point Bonded
2 | CAYUGA 230KV 5000 KCMIL | 1 | B | 60 | -1.755 | 3.9143 | 1 | Multicables 1 Point Bonded
3 | CAYUGA 230KV 5000 KCMIL | 1 | C | 60 | -0.755 | 3.9143 | 1 | Multicables 1 Point Bonded
4 | CAYUGA 230KV 5000 KCMIL | 1 | A | 60 | 0.755 | 3.9143 | 1 | Multicables 1 Point Bonded
5 | CAYUGA 230KV 5000 KCMIL | 1 | B | 60 | 1.755 | 3.9143 | 1 | Multicables 1 Point Bonded
6 | CAYUGA 230KV 5000 KCMIL | 1 | C | 60 | 2.755 | 3.9143 | 1 | Multicables 1 Point Bonded
Ampacity and Temperatures
Cable | Cable ID | I [A] | θc [°C] | θs [°C] | θa [°C] | θsurf [°C] | θduct [°C] | θair / θcasing [°C]
Cable Index Number | Cable Equipment ID | Steady State Ampacity | Conductor temperature | Sheath/Shield temperature | Armour temperature | Cable surface temperature | Duct surface temperature | Mean air temperature in the tunnel / Casing surface temperature
1 | CAYUGA 230KV 5000 KCMIL | 1288 | 80.6159 | 73.4022 | n/a | 71.6963 | 65.3182 | n/a
2 | CAYUGA 230KV 5000 KCMIL | 1288 | 86.7055 | 79.4037 | n/a | 77.7912 | 71.3497 | n/a
3 | CAYUGA 230KV 5000 KCMIL | 1288 | 88.4009 | 81.0763 | n/a | 79.337 | 73.1064 | n/a
4 | CAYUGA 230KV 5000 KCMIL | 1288 | 88.4046 | 81.08 | n/a | 79.3414 | 73.1085 | n/a
5 | CAYUGA 230KV 5000 KCMIL | 1288 | 86.7081 | 79.4063 | n/a | 77.793 | 71.3513 | n/a
6 | CAYUGA 230KV 5000 KCMIL | 1288 | 80.6224 | 73.4087 | n/a | 71.7028 | 65.3236 | n/a
Electrical Resistances
Cable | Cable ID | R₀ [Ω/mile] | ys | yp | R [Ω/mile] | R's [Ω/mile] | R'w [Ω/mile] | R'a [Ω/mile]
Cable Index Number | Cable Equipment ID | DC Resistance of the conductor at 20°C | Skin Effect Factor | Proximity Effect Factor | AC Resistance of Conductor at Operating Temperature | DC Resistance of Sheath at Operating Temperature | DC Resistance of Concentric Wires at Operating Temperature | DC Resistance of Armor at Operating Temperature
1 | CAYUGA 230KV 5000 KCMIL | 0.011162 | 0.41854 | 0.0052371 | 0.019677 | 0.70887 | 24.2647 | n/a
2 | CAYUGA 230KV 5000 KCMIL | 0.011162 | 0.40747 | 0.0070381 | 0.019927 | 0.72269 | 24.7378 | n/a
3 | CAYUGA 230KV 5000 KCMIL | 0.011162 | 0.40447 | 0.0070844 | 0.01999 | 0.72654 | 24.8696 | n/a
4 | CAYUGA 230KV 5000 KCMIL | 0.011162 | 0.40446 | 0.0070843 | 0.01999 | 0.72655 | 24.8699 | n/a
5 | CAYUGA 230KV 5000 KCMIL | 0.011162 | 0.40747 | 0.0070381 | 0.019927 | 0.7227 | 24.738 | n/a
6 | CAYUGA 230KV 5000 KCMIL | 0.011162 | 0.41853 | 0.0052369 | 0.019677 | 0.70889 | 24.2653 | n/a
Thermal Resistances
Cable | Cable ID | T₁ [K.m/W] | T₂ [K.m/W] | T₃ [K.m/W] | T₄' [K.m/W] | T₄'' [K.m/W] | T₄''' [K.m/W] | T₄ [K.m/W]
Cable Index Number | Cable Equipment ID | Thermal resistance of insulation | Thermal resistance of bedding | Thermal resistance of outer covering | Thermal resistance inside the duct | Thermal resistance of the duct | Thermal resistance of the external medium | Total external thermal resistance
1 | CAYUGA 230KV 5000 KCMIL | 0.34068 | 0 | 0.074098 | 0.21043 | 0.074104 | 1.6202 | 1.9047
2 | CAYUGA 230KV 5000 KCMIL | 0.34068 | 0 | 0.074098 | 0.20345 | 0.074104 | 1.8248 | 2.1023
3 | CAYUGA 230KV 5000 KCMIL | 0.34068 | 0 | 0.074098 | 0.20143 | 0.074104 | 1.9505 | 2.2261
4 | CAYUGA 230KV 5000 KCMIL | 0.34068 | 0 | 0.074098 | 0.20143 | 0.074104 | 1.9498 | 2.2254
5 | CAYUGA 230KV 5000 KCMIL | 0.34068 | 0 | 0.074098 | 0.20345 | 0.074104 | 1.8248 | 2.1023
6 | CAYUGA 230KV 5000 KCMIL | 0.34068 | 0 | 0.074098 | 0.21043 | 0.074104 | 1.6201 | 1.9046
Losses
Cable | Cable ID | Wc [W/ft] | Wd [W/ft] | Ws [W/ft] | Wa [W/ft] | Wt [W/ft] | ƛ₁ | ƛ₂
Cable Index Number | Cable Equipment ID | Conductor Losses | Dielectric Losses | Metallic Screen Losses | Armor/Pipe Losses | Total Losses | Screen Loss Factor | Armour Loss Factor + Pipe Loss Factor
1 | CAYUGA 230KV 5000 KCMIL | 6.1825 | 0.54297 | 0.10699 | 0 | 6.8324 | 0.017306 | 0
2 | CAYUGA 230KV 5000 KCMIL | 6.2609 | 0.54297 | 0.26994 | 0 | 7.0739 | 0.043114 | 0
3 | CAYUGA 230KV 5000 KCMIL | 6.2808 | 0.54297 | 0.068535 | 0 | 6.8923 | 0.010912 | 0
4 | CAYUGA 230KV 5000 KCMIL | 6.2809 | 0.54297 | 0.071196 | 0 | 6.895 | 0.011335 | 0
5 | CAYUGA 230KV 5000 KCMIL | 6.261 | 0.54297 | 0.27014 | 0 | 7.0741 | 0.043146 | 0
6 | CAYUGA 230KV 5000 KCMIL | 6.1825 | 0.54297 | 0.10822 | 0 | 6.8337 | 0.017505 | 0
Complementary Information
Cable | Cable ID | Δθint [°C] | [A] | [µF/mile] | [Ω] | [Ω/mile] | [Ω/mile] | [V/A/mile]
Cable Index Number | Cable Equipment ID | Temperature rise due to surrounding heat sources | Induced current on Metallic Screen | Cable Capacitance | Surge Impedance | Reactance of Conductor | Reactance of Metallic Sheath | Voltage drop for Three Phase System
1 | CAYUGA 230KV 5000 KCMIL | 25.3482 | 0 | 0.4313 | 48.9139 | 0.38899 | 0 | 0.034082
2 | CAYUGA 230KV 5000 KCMIL | 30.521 | 0 | 0.4313 | 47.699 | 0.3699 | 0 | 0.034515
3 | CAYUGA 230KV 5000 KCMIL | 32.5298 | 0 | 0.4313 | 47.6522 | 0.36918 | 0 | 0.034624
4 | CAYUGA 230KV 5000 KCMIL | 32.5279 | 0 | 0.4313 | 47.6522 | 0.36918 | 0 | 0.034624
5 | CAYUGA 230KV 5000 KCMIL | 30.5251 | 0 | 0.4313 | 47.699 | 0.3699 | 0 | 0.034515
6 | CAYUGA 230KV 5000 KCMIL | 25.3505 | 0 | 0.4313 | 48.9139 | 0.38899 | 0 | 0.034082

## Study Summary
Study Summary
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | Case 3 Duct Bank 3 ft 2 ft sep
Date: |  | 1/8/2026 12:34:43 PM
General Simulation Data
Steady State Option | [8 empty] | Temperature
Consider Electrical interaction between circuits | [8 empty] | No
Induced currents in metallic layers as a fraction of conductor current (applied to all single phase circuits) : | [8 empty] | 0
Conductor Resistances Computation Option: | [8 empty] | IEC-228
Standard Settings Options
General guidance | [8 empty] | Custom
Factor on RAC due to magnetic armour | [8 empty] | CIGREGuidance
Factor on RAC due to magnetic duct | [8 empty] | CIGREGuidance
Factor on ƛ₁ due to magnetic armour | [8 empty] | CYMCAPGuidance
Factor on ƛ₁ due to magnetic duct | [8 empty] | CIGREGuidance
Factor on ƛ₂ due to ƛ'₁ | [8 empty] | CYMCAPGuidance
ƛ''₁ computation | [8 empty] | CIGREGuidance
ƛ₂pipe computation | [8 empty] | CYMCAPGuidance
Wd computation | [8 empty] | CIGREGuidance
T₂ computation | [8 empty] | CIGREGuidance
T₄ computation | [8 empty] | CYMCAPGuidance
Installation Type:Multiple Ductbanks/Backfills
Ambient Soil Temperature at Installation Depth [°C] | [8 empty] | 29
Native Soil Thermal Resistivity [K.m/W] | [8 empty] | 0.9
Consider Non-Isothermal Earth Surface | [8 empty] | No
Layer Name |  | X [ft] | Y [ft] | Width [ft] | Height [ft] | Thermal Resistivity [K.m/W]
NSTD DB1 |  | -1.755 | 3.75 | 3.5 | 1.5 | 0.6
Sub Base |  | 0 | 1 | 7 | 0.99 | 2.5
Gravel Bed |  | 0 | 4.75 | 7 | 0.5 | 2.5
NSTD DB2 |  | 1.755 | 3.75 | 3.5 | 1.5 | 0.6
FTB R |  | 0 | 2.2475 | 7 | 1.505 | 1
Asphalt |  | 0 | 0.2525 | 7 | 0.505 | 3.5
Results Summary
Cable No. | Cable ID | Circuit No. | Feeder ID | Cable Phase | Cable Frequency | Daily Load Factor | X coordinate [ft] | Y coordinate [ft] | Conductor temperature [°C] | Ampacity [A]
1 | CAYUGA 230KV 5000 KCMIL | 1 |  | A | 60 | 1 | -2.755 | 3.9143 | 80.6159 | 1288
2 | CAYUGA 230KV 5000 KCMIL | 1 |  | B | 60 | 1 | -1.755 | 3.9143 | 86.7055 | 1288
3 | CAYUGA 230KV 5000 KCMIL | 1 |  | C | 60 | 1 | -0.755 | 3.9143 | 88.4009 | 1288
4 | CAYUGA 230KV 5000 KCMIL | 1 |  | A | 60 | 1 | 0.755 | 3.9143 | 88.4046 | 1288
5 | CAYUGA 230KV 5000 KCMIL | 1 |  | B | 60 | 1 | 1.755 | 3.9143 | 86.7081 | 1288
6 | CAYUGA 230KV 5000 KCMIL | 1 |  | C | 60 | 1 | 2.755 | 3.9143 | 80.6224 | 1288

## Steady State Summary
Steady State Summary
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | Case 3 Duct Bank 3 ft 2 ft sep
Date: |  | 1/8/2026 12:34:43 PM
Simulation Data
Installation type: |  | Multiple Ductbanks
Steady State Option |  | Temperature
Ambient temperature [°C] |  | 29
Native Soil Thermal Resistivity [K.m/W] |  | 0.9
Consider Non-Isothermal Earth Surface |  | No
Consider effect of soil dry out |  | No
Consider Electrical interaction between circuits |  | No
Induced current in metallic layers as a fraction of conductor current (applied to all single phase circuits) [A] |  | 0
Variable | Description |  | Unit | Cables
Cable No. | Cable Index Number |  |  | 1 | 2 | 3 | 4 | 5 | 6
General Input Data
Cable ID | Cable Equipment ID |  |  | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL
Circuit No. | Circuit No. | bar: Cables 1 to Cables 6
Phase | Cable Phase |  |  | A | B | C | A | B | C
Fq | Operating Frequency |  | [Hz] | 60 | 60 | 60 | 60 | 60 | 60
x | X coordinate |  | [ft] | -2.755 | -1.755 | -0.755 | 0.755 | 1.755 | 2.755
y | Y coordinate |  | [ft] | 3.9143 | 3.9143 | 3.9143 | 3.9143 | 3.9143 | 3.9143
DLF | Daily Load Factor |  | [p.u.] | bar: Cables 1 to Cables 6
| Bonding Type |  |  | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded
Ampacity
I | Steady State Ampacity |  | [A] | 1288 | 1288 | 1288 | 1288 | 1288 | 1288
I₀ | Steady State Ampacity without insulation temperature drop constraint |  | [A] | n/a | n/a | n/a | n/a | n/a | n/a
Temperatures
θc | Conductor temperature |  | [°C] | 80.6159 | 86.7055 | 88.4009 | 88.4046 | 86.7081 | 80.6224
Δθins | Temperature drop across the insulation |  | [°C] | n/a | n/a | n/a | n/a | n/a | n/a
θs | Sheath/Shield temperature |  | [°C] | 73.4022 | 79.4037 | 81.0763 | 81.08 | 79.4063 | 73.4087
θa | Armour temperature |  | [°C] | n/a | n/a | n/a | n/a | n/a | n/a
θsurf | Cable surface temperature |  | [°C] | 71.6963 | 77.7912 | 79.337 | 79.3414 | 77.793 | 71.7028
θduct | Duct surface temperature |  | [°C] | 65.3182 | 71.3497 | 73.1064 | 73.1085 | 71.3513 | 65.3236
Resistances
R₀ | DC Resistance of the conductor at 20°C |  | [Ω/mile] | 0.011162 | 0.011162 | 0.011162 | 0.011162 | 0.011162 | 0.011162
R | AC Resistance of the Conductor at Operating Temperature |  | [Ω/mile] | 0.019677 | 0.019927 | 0.01999 | 0.01999 | 0.019927 | 0.019677
ys | Skin Effect Factor |  |  | 0.41854 | 0.40747 | 0.40447 | 0.40446 | 0.40747 | 0.41853
yp | Proximity Effect Factor |  |  | 0.0052371 | 0.0070381 | 0.0070844 | 0.0070843 | 0.0070381 | 0.0052369
Losses
Wc | Conductor Losses |  | [W/ft] | 6.1825 | 6.2609 | 6.2808 | 6.2809 | 6.261 | 6.1825
Wd | Dielectric Losses |  | [W/ft] | 0.54297 | 0.54297 | 0.54297 | 0.54297 | 0.54297 | 0.54297
Ws | Metallic Screen Losses |  | [W/ft] | 0.10699 | 0.26994 | 0.068535 | 0.071196 | 0.27014 | 0.10822
Wa | Armor/Pipe Losses |  | [W/ft] | 0 | 0 | 0 | 0 | 0 | 0
Wt | Total Losses |  | [W/ft] | 6.8324 | 7.0739 | 6.8923 | 6.895 | 7.0741 | 6.8337
ƛ₁ | Screen Loss Factor |  |  | 0.017306 | 0.043114 | 0.010912 | 0.011335 | 0.043146 | 0.017505
ƛ₂ | Armour Loss Factor + Pipe Loss Factor |  |  | 0 | 0 | 0 | 0 | 0 | 0
Thermal resistances
T1 | Thermal Resistance Between Conductor and Screen |  | [K.m/W] | 0.34068 | 0.34068 | 0.34068 | 0.34068 | 0.34068 | 0.34068
T2 | Thermal Resistance Between Screen and Armour |  | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
T3 | Thermal Resistance of the Jacket/Pipe Coating |  | [K.m/W] | 0.074098 | 0.074098 | 0.074098 | 0.074098 | 0.074098 | 0.074098
T4 | Total external thermal resistance |  | [K.m/W] | 1.9047 | 2.1023 | 2.2261 | 2.2254 | 2.1023 | 1.9046
Others
Δθint | Temperature rise due to surrounding heat sources |  | [°C] | 25.3482 | 30.521 | 32.5298 | 32.5279 | 30.5251 | 25.3505
| Induced Voltage (standing) on Sheath |  | [V/mile] | 303.8686 | 248.4793 | 270.2795 | 268.902 | 251.6684 | 302.2447
| Induced Voltage angle on Sheath |  | [°] | -15.8563 | 87.9134 | -161.7172 | -17.5285 | 92.0694 | -165.1697
| Induced Voltage (standing) on Concentric Wires |  | [V/mile] | 302.2693 | 246.6297 | 268.2638 | 266.8966 | 249.8208 | 300.6606
| Induced Voltage angle on Concentric Wires |  | [°] | -15.7549 | 87.8723 | -161.7819 | -17.4615 | 92.1098 | -165.2739
| Induced current on Metallic Screen |  | [A] | 0 | 0 | 0 | 0 | 0 | 0

## Cable - CA...A 230KV 5000 KCMIL
Cables Report
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | Case 3 Duct Bank 3 ft 2 ft sep
Date: |  | 1/8/2026 12:34:43 PM
No. | Description |  | Unit | 1
General Cable Information
1 | Cable Equipment ID |  |  | CAYUGA 230KV 5000 KCMIL
2 | Number of Cores |  |  | Single Core
3 | Voltage |  | [kV] | 230
4 | Conductor Area |  | [in²] | 3.9302
5 | Cable Overall Diameter |  | [in] | 5.4595
6 | Maximum Steady-State Conductor Temperature |  | [°C] | 90
7 | Maximum Emergency Conductor Temperature |  | [°C] | 110
Conductor
8 | Material |  |  | Copper
9 | Electrical Resistivity at 20°C |  | [µΩ.cm] | 1.7241
10 | Temperature Coefficient at 20°C |  | [1/K] | 0.00393
11 | Reciprocal of Temperature Coefficient of Resistance (BETA) |  | [K] | 234.4529
12 | Volumetric Specific Heat (SH) |  | [J/(K*cm³)] | 3.45
13 | Construction |  |  | 6 Segments
14 | Conductor Insulation System |  |  | Extruded
15 | Milliken Wires Construction |  |  | Bare Unidirectional Wires
16 | Ks (Skin Effect Coefficient) |  |  | 0.62
17 | Kp (Proximity Effect Coefficient) |  |  | 0.37
18 | Diameter |  | [in] | 2.48
Conductor Shield
19 | Thickness |  | [in] | 0.094
20 | Diameter |  | [in] | 2.668
Insulation
21 | Material |  |  | XLPE Unfilled
22 | Thermal Resistivity |  | [K.m/W] | 3.5
23 | Dielectric Loss Factor - ( tan delta ) |  |  | 0.001
24 | Relative Permittivity - ( epsilon ) |  |  | 2.5
25 | Specific Insulation Resistance Constant at 60°F - ( K ) |  | [㏁.1000ft] | 1858.0608
26 | Thickness |  | [in] | 0.906
27 | Diameter |  | [in] | 4.48
Insulation Screen
28 | Material |  |  | Semi Conducting Screen
29 | Thickness |  | [in] | 0.094
30 | Diameter |  | [in] | 4.668
Sheath
31 | Is Sheath Around Each Core? |  |  | n/a
32 | Material |  |  | Copper
33 | Electrical Resistivity at 20°C |  | [µΩ.cm] | 1.7241
34 | Temperature Coefficient at 20°C |  | [1/K] | 0.00393
35 | Reciprocal of Temperature Coefficient of Resistance (BETA) |  | [K] | 234.5
36 | Volumetric Specific Heat (SH) |  | [J/(K*cm³)] | 3.45
37 | Corrugation Type |  |  | Non Corrugated
38 | Thickness |  | [in] | 0.005
39 | Diameter |  | [in] | 4.678
Concentric neutral/Skid wires
40 | Are Concentric Neutral Wires Around Each Core? |  |  | n/a
41 | Material |  |  | Copper
42 | Electrical Resistivity at 20°C |  | [µΩ.cm] | 1.7241
43 | Temperature Coefficient at 20°C |  | [1/K] | 0.00393
44 | Reciprocal of Temperature Coefficient of Resistance (BETA) |  | [K] | 234.5
45 | Volumetric Specific Heat (SH) |  | [J/(K*cm³)] | 3.45
46 | Wire Type |  |  | Round Wires
47 | Length of Lay |  | [in] | 0.3937
48 | Number of Wires |  |  | 40
49 | Wire Gauge |  |  | 16
50 | Thickness |  | [in] | 0.05076
51 | Diameter |  | [in] | 4.7795
Jacket
52 | Material |  |  | Polyethylene
53 | Thermal Resistivity |  | [K.m/W] | 3.5
54 | Thickness |  | [in] | 0.34
55 | Diameter |  | [in] | 5.4595
No. | Description |  | Unit | 1
Specific Installation Data
56 | Cable Equipment ID |  |  | CAYUGA 230KV 5000 KCMIL
57 | Cable Frequency |  | [Hz] | 60
58 | Sheath / Shield Bonding |  |  | Multicables 1 Point Bonded
59 | Loss Factor Constant (ALOS) |  |  | 0.3
60 | Conduit construction |  |  | PVC Duct in Concrete
61 | Conduit material thermal resistivity |  | [K.m/W] | 6
62 | Conduit filling material |  |  | Air
63 | Inner diameter of the conduit |  | [in] | 7.981
64 | Outer diameter of the conduit |  | [in] | 8.625
Cable ID : CAYUGA 230KV 5000 KCMIL
Cable Title |  | CAYUGA 230KV 5000 kcmil

## Impedances
Cable Impedances & Admittances
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | Case 3 Duct Bank 3 ft 2 ft sep
Date: |  | 1/8/2026 12:34:43 PM
Earth Resistivity: [Ω.m] |  | 100
Frequency: [Hz] |  | 60
Temperature
Circuit 1
|  |  | Conductor | [5 empty] | Sheath | [5 empty] | Concentric neutral/Skid wires
|  | Phase | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C
| Temperature | [°C] | 80.6159 | 88.4046 | 86.7055 | 86.7081 | 88.4009 | 80.6224 | 73.4022 | 81.08 | 79.4037 | 79.4063 | 81.0763 | 73.4087 | 73.4022 | 81.08 | 79.4037 | 79.4063 | 81.0763 | 73.4087
R_Primitive [Ω/mile]
Circuit No. 1
|  |  | Conductor | [5 empty] | Sheath | [5 empty] | Concentric neutral/Skid wires
|  | Phase | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C
Circuit No. 1 | Conductor | A | 0.11498 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.11523 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.11523 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.11523 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11523 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11523 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| Sheath | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.80417 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.81799 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.81799 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.81799 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.81799 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.81799 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| Concentric neutral Skid wires | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 24.3601 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 24.8331 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 24.8331 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 24.8331 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 24.8331 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 24.8331
X Primitive [Ω/mile]
Circuit No. 1
|  |  | Conductor | [5 empty] | Sheath | [5 empty] | Concentric neutral/Skid wires
|  | Phase | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C
Circuit No. 1 | Conductor | A | 1.2685 | 0.81036 | 0.96265 | 0.77992 | 0.87854 | 0.75561 | 1.1613 | 0.81036 | 0.96265 | 0.77992 | 0.87854 | 0.75561 | 1.1598 | 0.81036 | 0.96265 | 0.77992 | 0.87854 | 0.75561
|  | A | 0.81036 | 1.2685 | 0.85107 | 0.96265 | 0.91279 | 0.87854 | 0.81036 | 1.1613 | 0.85107 | 0.96265 | 0.91279 | 0.87854 | 0.81036 | 1.1598 | 0.85107 | 0.96265 | 0.91279 | 0.87854
|  | B | 0.96265 | 0.85107 | 1.2685 | 0.81036 | 0.96265 | 0.77992 | 0.96265 | 0.85107 | 1.1613 | 0.81036 | 0.96265 | 0.77992 | 0.96265 | 0.85107 | 1.1598 | 0.81036 | 0.96265 | 0.77992
|  | B | 0.77992 | 0.96265 | 0.81036 | 1.2685 | 0.85107 | 0.96265 | 0.77992 | 0.96265 | 0.81036 | 1.1613 | 0.85107 | 0.96265 | 0.77992 | 0.96265 | 0.81036 | 1.1598 | 0.85107 | 0.96265
|  | C | 0.87854 | 0.91279 | 0.96265 | 0.85107 | 1.2685 | 0.81036 | 0.87854 | 0.91279 | 0.96265 | 0.85107 | 1.1613 | 0.81036 | 0.87854 | 0.91279 | 0.96265 | 0.85107 | 1.1598 | 0.81036
|  | C | 0.75561 | 0.87854 | 0.77992 | 0.96265 | 0.81036 | 1.2685 | 0.75561 | 0.87854 | 0.77992 | 0.96265 | 0.81036 | 1.1613 | 0.75561 | 0.87854 | 0.77992 | 0.96265 | 0.81036 | 1.1598
| Sheath | A | 1.1613 | 0.81036 | 0.96265 | 0.77992 | 0.87854 | 0.75561 | 1.1613 | 0.81036 | 0.96265 | 0.77992 | 0.87854 | 0.75561 | 1.1598 | 0.81036 | 0.96265 | 0.77992 | 0.87854 | 0.75561
|  | A | 0.81036 | 1.1613 | 0.85107 | 0.96265 | 0.91279 | 0.87854 | 0.81036 | 1.1613 | 0.85107 | 0.96265 | 0.91279 | 0.87854 | 0.81036 | 1.1598 | 0.85107 | 0.96265 | 0.91279 | 0.87854
|  | B | 0.96265 | 0.85107 | 1.1613 | 0.81036 | 0.96265 | 0.77992 | 0.96265 | 0.85107 | 1.1613 | 0.81036 | 0.96265 | 0.77992 | 0.96265 | 0.85107 | 1.1598 | 0.81036 | 0.96265 | 0.77992
|  | B | 0.77992 | 0.96265 | 0.81036 | 1.1613 | 0.85107 | 0.96265 | 0.77992 | 0.96265 | 0.81036 | 1.1613 | 0.85107 | 0.96265 | 0.77992 | 0.96265 | 0.81036 | 1.1598 | 0.85107 | 0.96265
|  | C | 0.87854 | 0.91279 | 0.96265 | 0.85107 | 1.1613 | 0.81036 | 0.87854 | 0.91279 | 0.96265 | 0.85107 | 1.1613 | 0.81036 | 0.87854 | 0.91279 | 0.96265 | 0.85107 | 1.1598 | 0.81036
|  | C | 0.75561 | 0.87854 | 0.77992 | 0.96265 | 0.81036 | 1.1613 | 0.75561 | 0.87854 | 0.77992 | 0.96265 | 0.81036 | 1.1613 | 0.75561 | 0.87854 | 0.77992 | 0.96265 | 0.81036 | 1.1598
| Concentric neutral Skid wires | A | 1.1598 | 0.81036 | 0.96265 | 0.77992 | 0.87854 | 0.75561 | 1.1598 | 0.81036 | 0.96265 | 0.77992 | 0.87854 | 0.75561 | 1.1632 | 0.81036 | 0.96265 | 0.77992 | 0.87854 | 0.75561
|  | A | 0.81036 | 1.1598 | 0.85107 | 0.96265 | 0.91279 | 0.87854 | 0.81036 | 1.1598 | 0.85107 | 0.96265 | 0.91279 | 0.87854 | 0.81036 | 1.1632 | 0.85107 | 0.96265 | 0.91279 | 0.87854
|  | B | 0.96265 | 0.85107 | 1.1598 | 0.81036 | 0.96265 | 0.77992 | 0.96265 | 0.85107 | 1.1598 | 0.81036 | 0.96265 | 0.77992 | 0.96265 | 0.85107 | 1.1632 | 0.81036 | 0.96265 | 0.77992
|  | B | 0.77992 | 0.96265 | 0.81036 | 1.1598 | 0.85107 | 0.96265 | 0.77992 | 0.96265 | 0.81036 | 1.1598 | 0.85107 | 0.96265 | 0.77992 | 0.96265 | 0.81036 | 1.1632 | 0.85107 | 0.96265
|  | C | 0.87854 | 0.91279 | 0.96265 | 0.85107 | 1.1598 | 0.81036 | 0.87854 | 0.91279 | 0.96265 | 0.85107 | 1.1598 | 0.81036 | 0.87854 | 0.91279 | 0.96265 | 0.85107 | 1.1632 | 0.81036
|  | C | 0.75561 | 0.87854 | 0.77992 | 0.96265 | 0.81036 | 1.1598 | 0.75561 | 0.87854 | 0.77992 | 0.96265 | 0.81036 | 1.1598 | 0.75561 | 0.87854 | 0.77992 | 0.96265 | 0.81036 | 1.1632
R Bonding [Ω/mile]
Circuit No. 1
Conductor
|  | Phase | A | A | B | B | C | C
Circuit No. 1 | Conductor | A | 0.11498 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.11523 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.11523 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.11523 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11523 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11523
X Bonding [Ω/mile]
Circuit No. 1
Conductor
|  | Phase | A | A | B | B | C | C
Circuit No. 1 | Conductor | A | 1.2685 | 0.81036 | 0.96265 | 0.77992 | 0.87854 | 0.75561
|  | A | 0.81036 | 1.2685 | 0.85107 | 0.96265 | 0.91279 | 0.87854
|  | B | 0.96265 | 0.85107 | 1.2685 | 0.81036 | 0.96265 | 0.77992
|  | B | 0.77992 | 0.96265 | 0.81036 | 1.2685 | 0.85107 | 0.96265
|  | C | 0.87854 | 0.91279 | 0.96265 | 0.85107 | 1.2685 | 0.81036
|  | C | 0.75561 | 0.87854 | 0.77992 | 0.96265 | 0.81036 | 1.2685
R Phase [Ω/mile]
Circuit No. 1
|  | A | A | B | B | C | C
Circuit No. 1 | A | 0.11498 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| A | 0.095302 | 0.11523 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.11523 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.095302 | 0.11523 | 0.095302 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11523 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11523
X Phase [Ω/mile]
Circuit No. 1
|  | A | A | B | B | C | C
Circuit No. 1 | A | 1.2685 | 0.81036 | 0.96265 | 0.77992 | 0.87854 | 0.75561
| A | 0.81036 | 1.2685 | 0.85107 | 0.96265 | 0.91279 | 0.87854
| B | 0.96265 | 0.85107 | 1.2685 | 0.81036 | 0.96265 | 0.77992
| B | 0.77992 | 0.96265 | 0.81036 | 1.2685 | 0.85107 | 0.96265
| C | 0.87854 | 0.91279 | 0.96265 | 0.85107 | 1.2685 | 0.81036
| C | 0.75561 | 0.87854 | 0.77992 | 0.96265 | 0.81036 | 1.2685
R Circuit [Ω/mile]
Circuit No. 1
|  | A | B | C
Circuit No. 1 | A | 0.10548 | 0.095458 | 0.095366
| B | 0.095458 | 0.10541 | 0.095463
| C | 0.095366 | 0.095463 | 0.10555
X Circuit [Ω/mile]
Circuit No. 1
|  | A | B | C
Circuit No. 1 | A | 1.0324 | 0.8857 | 0.85593
| B | 0.8857 | 1.0364 | 0.8857
| C | 0.85593 | 0.8857 | 1.0324
R Sequence [Ω/mile]
Circuit No. 1
|  | 0 | 1 | 2
Circuit No. 1 | 0 | 0.29634 | 0.00972 | -0.009752
| 1 | -0.009752 | 0.010051 | -0.016013
| 2 | 0.00972 | 0.016083 | 0.010051
X Sequence [Ω/mile]
Circuit No. 1
|  | 0 | 1 | 2
Circuit No. 1 | 0 | 2.7853 | -0.005609 | -0.005633
| 1 | -0.005633 | 0.15794 | 0.009358
| 2 | -0.005609 | 0.009173 | 0.15794
R Sequence/R1
Circuit No. 1
|  | 0 | 1 | 2
Circuit No. 1 | 0 | 29.4829 | 0.96705 | 0.97018
| 1 | 0.97018 | 1 | 1.5931
| 2 | 0.96705 | 1.6001 | 1
X Sequence/X1
Circuit No. 1
|  | 0 | 1 | 2
Circuit No. 1 | 0 | 17.6351 | 0.035511 | 0.035669
| 1 | 0.035669 | 1 | 0.059249
| 2 | 0.035511 | 0.05808 | 1
Symmetrical Components [Ω/mile]
Circuit | Z0 | Z1 | Z2
1 | 0.296339 + j 2.785276 | 0.010051 + j 0.15794 | 0.010051 + j 0.15794
Y Primitive [µS/mile]
Circuit No. 1
A | A | B | B | C | C
0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781
Y Circuit [µS/mile]
Circuit No. 1
A | B | C
0.32546 + j 325.459561 | 0.32546 + j 325.459561 | 0.32546 + j 325.459561
Y Sequence [µS/mile]
Circuit No. 1
0 | 1 | 2
0.32546 + j 325.459561 | 0.32546 + j 325.459561 | 0.32546 + j 325.459561

## Electrical Parameters
Electrical Parameters
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | Case 3 Duct Bank 3 ft 2 ft sep
Date: |  | 1/8/2026 12:34:43 PM
No. | Description |  | Unit | Cable No.1 | Cable No.2 | Cable No.3 | Cable No.4 | Cable No.5 | Cable No.6
1 | Cable Equipment ID |  |  | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL
Resistances
2 | DC Resistance of the conductor at 20°C |  | [Ω/mile] | 0.011162 | 0.011162 | 0.011162 | 0.011162 | 0.011162 | 0.011162
DC Resistance of the conductor at 20°C Equation
3 | DC Resistance of Conductor at Operating Temperature |  | [Ω/mile] | 0.01382 | 0.014088 | 0.014162 | 0.014162 | 0.014088 | 0.013821
DC Resistance of Conductor at Operating Temperature Equation
4 | AC Resistance of Conductor at 20°C |  | [Ω/mile] | 0.01746 | 0.017486 | 0.017488 | 0.017488 | 0.017486 | 0.01746
5 | AC Resistance of Conductor at Operating Temperature |  | [Ω/mile] | 0.019677 | 0.019927 | 0.01999 | 0.01999 | 0.019927 | 0.019677
AC Resistance of Conductor at Operating Temperature Equation
6 | DC Resistance of Sheath at 20°C |  | [Ω/mile] | 0.58591 | 0.58591 | 0.58591 | 0.58591 | 0.58591 | 0.58591
7 | DC Resistance of Sheath at Operating Temperature |  | [Ω/mile] | 0.70887 | 0.72269 | 0.72654 | 0.72655 | 0.7227 | 0.70889
DC Resistance of Sheath at Operating Temperature Equation
8 | DC Resistance of Concentric Wires at 20°C |  | [Ω/mile] | 20.0557 | 20.0557 | 20.0557 | 20.0557 | 20.0557 | 20.0557
9 | DC Resistance of Concentric Wires at Operating Temperature |  | [Ω/mile] | 24.2647 | 24.7378 | 24.8696 | 24.8699 | 24.738 | 24.2653
DC Resistance of Concentric Wires at Operating Temperature Equation
Losses
10 | Conductor Losses |  | [W/ft] | 6.1825 | 6.2609 | 6.2808 | 6.2809 | 6.261 | 6.1825
Conductor Losses Equation
11 | Dielectric Losses |  | [W/ft] | 0.54297 | 0.54297 | 0.54297 | 0.54297 | 0.54297 | 0.54297
Dielectric Losses Equation
12 | Metallic Screen Losses |  | [W/ft] | 0.10699 | 0.26994 | 0.068535 | 0.071196 | 0.27014 | 0.10822
Metallic Screen Losses Equation
13 | Armor/Pipe Losses |  | [W/ft] | 0 | 0 | 0 | 0 | 0 | 0
Armor/Pipe Losses Equation
14 | Total Losses |  | [W/ft] | 6.8324 | 7.0739 | 6.8923 | 6.895 | 7.0741 | 6.8337
Total Losses Equation
Capacitance, Inductance, Impedance
15 | Capacitance |  | [µF/mile] | 0.4313 | 0.4313 | 0.4313 | 0.4313 | 0.4313 | 0.4313
Capacitance Equation
16 | Inductance of Conductor |  | [mH/mile] | 1.0318 | 0.9812 | 0.97928 | 0.97928 | 0.9812 | 1.0318
Inductance of Conductor Equation
17 | Reactance of Conductor |  | [Ω/mile] | 0.38899 | 0.3699 | 0.36918 | 0.36918 | 0.3699 | 0.38899
Reactance of Conductor Equation
18 | Inductance of Metallic Sheath |  | [mH/mile] | 0 | 0 | 0 | 0 | 0 | 0
Inductance of Metallic Sheath Equation
19 | Reactance of Metallic Sheath |  | [Ω/mile] | 0 | 0 | 0 | 0 | 0 | 0
Reactance of Metallic Sheath Equation
20 | Positive Sequence Impedance |  | [Ω/mile] | 0.019677 + j0.388988 | 0.019927 + j0.369904 | 0.019990 + j0.369180 | 0.019990 + j0.369180 | 0.019927 + j0.369904 | 0.019677 + j0.388988
Positive Sequence Impedance Equation
21 | Negative Sequence Impedance |  | [Ω/mile] | 0.019677 + j0.388988 | 0.019927 + j0.369904 | 0.019990 + j0.369180 | 0.019990 + j0.369180 | 0.019927 + j0.369904 | 0.019677 + j0.388988
Negative Sequence Impedance Equation
22 | Zero Sequence Impedance |  | [Ω/mile] | 0.585109 + j0.107934 | 0.584985 + j0.107934 | 0.584952 + j0.107934 | 0.584952 + j0.107934 | 0.584985 + j0.107934 | 0.585109 + j0.107934
Zero Sequence Impedance Equation
23 | Surge Impedance |  | [Ω] | 48.9139 | 47.699 | 47.6522 | 47.6522 | 47.699 | 48.9139
Surge Impedance Equation
Others
24 | Dielectric Stress at Insulation Inner Surface |  | [kV/in] | 192.0593 | 192.0593 | 192.0593 | 192.0593 | 192.0593 | 192.0593
Dielectric Stress at Insulation Inner Surface Equation
25 | Dielectric Stress at Insulation Outer Surface |  | [kV/in] | 114.3782 | 114.3782 | 114.3782 | 114.3782 | 114.3782 | 114.3782
26 | Insulation Resistance at 60°F (15.8°C) |  | [㏁.1000ft] | 418.235 | 418.235 | 418.235 | 418.235 | 418.235 | 418.235
Insulation Resistance at 60°F (15.8°C) Equation
27 | Reduction Factor (2pt bonded & single metallic screen) |  |  | n/a | n/a | n/a | n/a | n/a | n/a
Reduction Factor Equation (2pt bonded & single metallic screen)
28 | Charging Current for One Cable (Phase) |  | [A/mile] | 21.5893 | 21.5893 | 21.5893 | 21.5893 | 21.5893 | 21.5893
Charging Current Equation for One Cable (Phase)
29 | Charging Capacity of three phase system at Uo |  | [kvar/mile] | 8600.5667 | 8600.5667 | 8600.5667 | 8600.5667 | 8600.5667 | 8600.5667
Charging Capacity of three phase system at Uo Equation
30 | Voltage drop for Three Phase System |  | [V/A/mile] | 0.034082 | 0.034515 | 0.034624 | 0.034624 | 0.034515 | 0.034082
Voltage drop Equation for Three Phase System
31 | Induced Voltage (standing) on Sheath |  | [V/mile] | 303.8686 | 248.4793 | 270.2795 | 268.902 | 251.6684 | 302.2447
32 | Induced Voltage angle on Sheath |  | [°] | -15.8563 | 87.9134 | -161.7172 | -17.5285 | 92.0694 | -165.1697
33 | Induced Voltage (standing) on Concentric Wires |  | [V/mile] | 302.2693 | 246.6297 | 268.2638 | 266.8966 | 249.8208 | 300.6606
34 | Induced Voltage angle on Concentric Wires |  | [°] | -15.7549 | 87.8723 | -161.7819 | -17.4615 | 92.1098 | -165.2739
35 | Induced current on Metallic Screen |  | [A] | 0 | 0 | 0 | 0 | 0 | 0
Induced current on Metallic Screen Equation

## Steady State
Cable Parameters under Normal Operation
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | Case 3 Duct Bank 3 ft 2 ft sep
Date: |  | 1/8/2026 12:34:43 PM
No. | Symbol | Description | Unit | Cable No.1 | Cable No.2 | Cable No.3 | Cable No.4 | Cable No.5 | Cable No.6
1 |  | Cable Equipment ID |  | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL
Normal Operation IEC 60287-1-1
Conductor AC Resistance
2 | R₀ | DC Resistance of the conductor at 20°C | [Ω/mile] | 0.011162 | 0.011162 | 0.011162 | 0.011162 | 0.011162 | 0.011162
DC Resistance of the conductor at 20°C Equation
3 | R' | DC Resistance of Conductor at Operating Temperature | [Ω/mile] | 0.01382 | 0.014088 | 0.014162 | 0.014162 | 0.014088 | 0.013821
DC Resistance of Conductor at Operating Temperature Equation
4 | dc | Conductor Diameter | [in] | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48
5 | s | Distance Between Conductor Axes | [in] | 23.8273 | 20.3598 | 20.2386 | 20.2386 | 20.3598 | 23.8273
6 | ks | Factor Used for xs Calculation (Skin Effect) |  | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62
7 | kp | Factor Used for xp Calculation (Proximity Effect) |  | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37
8 | Xs² | Component of Ys Calculation (Skin Effect) |  | 10.887 | 10.6806 | 10.6245 | 10.6244 | 10.6805 | 10.8868
Component of Ys Calculation (Skin Effect) Equation
9 | Xp² | Component of Yp Calculation (Proximity Effect) |  | 6.4971 | 6.3739 | 6.3404 | 6.3404 | 6.3738 | 6.497
Component of Yp Calculation (Proximity Effect) Equation
10 | ys | Skin Effect Factor |  | 0.41854 | 0.40747 | 0.40447 | 0.40446 | 0.40747 | 0.41853
Skin Effect Factor Equation
11 | yp | Proximity Effect Factor |  | 0.0052371 | 0.0070381 | 0.0070844 | 0.0070843 | 0.0070381 | 0.0052369
Proximity Effect Factor Equation
12 | R | AC Resistance of Conductor at Operating Temperature | [Ω/mile] | 0.019677 | 0.019927 | 0.01999 | 0.01999 | 0.019927 | 0.019677
AC Resistance of Conductor at Operating Temperature Equation
Dielectric Losses
13 | tanδ | Dielectric Loss Factor |  | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001
14 | ε | Insulation Relative Permittivity |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
15 | C | Cable Capacitance | [µF/mile] | 0.4313 | 0.4313 | 0.4313 | 0.4313 | 0.4313 | 0.4313
Cable Capacitance Equation
16 | U₀ | Voltage | [kV] | 132.7906 | 132.7906 | 132.7906 | 132.7906 | 132.7906 | 132.7906
17 | Wd | Cable Dielectric Losses Per Phase | [W/ft] | 0.54297 | 0.54297 | 0.54297 | 0.54297 | 0.54297 | 0.54297
Cable Dielectric Losses Per Phase Equation
Filament method
18 | ƛ'₁ | Screen Loss Factor Caused by Circulating Current |  | 0 | 0 | 0 | 0 | 0 | 0
19 | ƛ''₁ | Screen Loss Factor Caused by Eddy Current |  | 0.017306 | 0.043114 | 0.010912 | 0.011335 | 0.043146 | 0.017505
20 | ƛ₁ | Screen Loss Factor |  | 0.017306 | 0.043114 | 0.010912 | 0.011335 | 0.043146 | 0.017505
21 | ƛ₂a | Armour Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
22 | ƛ₂pipe | Pipe Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
23 | ƛ₂ | Armour Loss Factor + Pipe Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
Armour Loss Factor + Pipe Loss Factor Equation
Normal Operation IEC 60287-2-1
24 | T₁ | Thermal Resistance Between Conductor and Screen | [K.m/W] | 0.34068 | 0.34068 | 0.34068 | 0.34068 | 0.34068 | 0.34068
Thermal Resistance Between Conductor and Screen Equation
25 | t₁ | Insulation Thickness Between Conductor and Screen | [in] | 1.094 | 1.094 | 1.094 | 1.094 | 1.094 | 1.094
26 | ρTi | Thermal Resistivity of Insulation | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
27 | T₃ | Thermal Resistance of Jacket/Pipe Coating | [K.m/W] | 0.074098 | 0.074098 | 0.074098 | 0.074098 | 0.074098 | 0.074098
Thermal Resistance of Jacket/Pipe Coating Equation
28 | t₃ | Thickness of Jacket/Pipe Coating | [in] | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34
29 | ρTJ | Thermal Resistivity of Jacket/Pipe Coating | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
30 | T Conductor Shield | Thermal resistance | [K.m/W] | 0.029074 | 0.029074 | 0.029074 | 0.029074 | 0.029074 | 0.029074
31 |  | Thermal resistance equation
32 |  | Thermal resistivity | [K.m/W] | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
33 |  | Layer thickness | [in] | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094
34 |  | Internal diameter | [in] | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48
35 | T Insulation | Thermal resistance | [K.m/W] | 0.28871 | 0.28871 | 0.28871 | 0.28871 | 0.28871 | 0.28871
36 |  | Thermal resistance equation
37 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
38 |  | Layer thickness | [in] | 0.906 | 0.906 | 0.906 | 0.906 | 0.906 | 0.906
39 |  | Internal diameter | [in] | 2.668 | 2.668 | 2.668 | 2.668 | 2.668 | 2.668
40 | T Insulation Screen | Thermal resistance | [K.m/W] | 0.022899 | 0.022899 | 0.022899 | 0.022899 | 0.022899 | 0.022899
41 |  | Thermal resistance equation
42 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
43 |  | Layer thickness | [in] | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094
44 |  | Internal diameter | [in] | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48
45 | T Sheath | Thermal resistance | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
46 |  | Thermal resistance equation
47 |  | Thermal resistivity | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
48 |  | Layer thickness | [in] | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005
49 |  | Internal diameter | [in] | 4.668 | 4.668 | 4.668 | 4.668 | 4.668 | 4.668
50 | T Concentric wires | Thermal resistance | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
51 |  | Thermal resistance equation
52 |  | Thermal resistivity | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
53 |  | Layer thickness | [in] | 0.05076 | 0.05076 | 0.05076 | 0.05076 | 0.05076 | 0.05076
54 |  | Internal diameter | [in] | 4.678 | 4.678 | 4.678 | 4.678 | 4.678 | 4.678
55 | T Jacket | Thermal resistance | [K.m/W] | 0.074098 | 0.074098 | 0.074098 | 0.074098 | 0.074098 | 0.074098
56 |  | Thermal resistance equation
57 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
58 |  | Layer thickness | [in] | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34
59 |  | Internal diameter | [in] | 4.7795 | 4.7795 | 4.7795 | 4.7795 | 4.7795 | 4.7795
Thermal resistance inside the duct
60 | U | Constant from IEC6028721 clause4272 |  | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87
61 | V | Constant from IEC6028721 clause4272 |  | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312
62 | Y | Constant from IEC6028721 clause4272 |  | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037
63 | θm | Mean temperature of the medium in conduit | [°C] | 69.3825 | 75.324 | 77.1237 | 77.1258 | 75.3265 | 69.3883
64 | Deq | Equivalent diameter of the cables inside the conduit | [in] | 5.4595 | 5.4595 | 5.4595 | 5.4595 | 5.4595 | 5.4595
65 | T₄' | Thermal resistance of the medium in conduit | [K.m/W] | 0.21043 | 0.20345 | 0.20143 | 0.20143 | 0.20345 | 0.21043
Thermal resistance of the medium in conduit Equation
Thermal resistance of the duct
66 | Do | Outer diameter of the conduit | [in] | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625
67 | Di | Inner diameter of the conduit | [in] | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981
68 | ρT | Thermal resistivity of the conduit material | [K.m/W] | 6 | 6 | 6 | 6 | 6 | 6
69 | T₄'' | Thermal resistance of the conduit | [K.m/W] | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104
Thermal resistance of the conduit Equation
Thermal resistance of the external medium
70 | L | Depth of cable/conduit axis | [ft] | 3.9143 | 3.9143 | 3.9143 | 3.9143 | 3.9143 | 3.9143
71 | De / Do | External diameter of the cable conduit | [ft] | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875
72 | u | Geometric factor as per IEC60287-2-1 clause 4.2.2 |  | 10.8919 | 10.8919 | 10.8919 | 10.8919 | 10.8919 | 10.8919
Geometric factor Equation as per IEC60287-2-1 clause 4.2.2
73 | ρTs | Thermal resistivity of the soil | [K.m/W] | 0.99864 | 1.0401 | 1.0447 | 1.0446 | 1.0398 | 0.99873
74 | T₄'''self | Thermal resistance of the cable isolated | [K.m/W] | 0.48938 | 0.50968 | 0.51195 | 0.51193 | 0.50955 | 0.48942
Thermal resistance of the cable isolated Equation
75 | T₄'''mutual | Thermal resistance associated to the temperature rise due to surrounding heat sources | [K.m/W] | 1.1308 | 1.3151 | 1.4386 | 1.4379 | 1.3152 | 1.1307
Thermal resistance associated to the temperature rise due to surrounding heat sources Equation
76 | Δθint | Temperature rise due to surrounding heat sources | [°C] | 25.3482 | 30.521 | 32.5298 | 32.5279 | 30.5251 | 25.3505
Temperature rise due to surrounding heat sources Equation
77 | T₄''' | Thermal resistance of the external medium | [K.m/W] | 1.6202 | 1.8248 | 1.9505 | 1.9498 | 1.8248 | 1.6201
Thermal resistance of the external medium Equation
Thermal Capacitance IEC 853-2
78 | Q Conductor | Thermal capacitance | [J/m.K] | 8747.9442 | 8747.9442 | 8747.9442 | 8747.9442 | 8747.9442 | 8747.9442
79 |  | Thermal capacitance equation
80 |  | Material surface | [in²] | 3.9302 | 3.9302 | 3.9302 | 3.9302 | 3.9302 | 3.9302
81 |  | Volumetric specific heat of the material | [J/(K*m³)] | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000
82 | Q Conductor Shield | Thermal capacitance | [J/m.K] | 1176.969 | 1176.969 | 1176.969 | 1176.969 | 1176.969 | 1176.969
83 |  | Thermal capacitance equation
84 |  | External diameter | [in] | 2.668 | 2.668 | 2.668 | 2.668 | 2.668 | 2.668
85 |  | Internal diameter | [in] | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48
86 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
87 | Q1 Insulation | Thermal capacitance | [J/m.K] | 5879.1234 | 5879.1234 | 5879.1234 | 5879.1234 | 5879.1234 | 5879.1234
88 |  | Thermal capacitance equation
89 |  | External diameter | [in] | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48
90 |  | Internal diameter | [in] | 2.668 | 2.668 | 2.668 | 2.668 | 2.668 | 2.668
91 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
92 | Q2 Insulation | Thermal capacitance | [J/m.K] | 9871.9913 | 9871.9913 | 9871.9913 | 9871.9913 | 9871.9913 | 9871.9913
93 |  | Thermal capacitance equation
94 |  | External diameter | [in] | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48
95 |  | Internal diameter | [in] | 2.668 | 2.668 | 2.668 | 2.668 | 2.668 | 2.668
96 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
97 | Q Insulation Screen | Thermal capacitance | [J/m.K] | 2091.4738 | 2091.4738 | 2091.4738 | 2091.4738 | 2091.4738 | 2091.4738
98 |  | Thermal capacitance equation
99 |  | External diameter | [in] | 4.668 | 4.668 | 4.668 | 4.668 | 4.668 | 4.668
100 |  | Internal diameter | [in] | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48
101 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
102 | Q Sheath | Thermal capacitance | [J/m.K] | 163.3798 | 163.3798 | 163.3798 | 163.3798 | 163.3798 | 163.3798
103 |  | Thermal capacitance equation
104 |  | External diameter | [in] | 4.678 | 4.678 | 4.678 | 4.678 | 4.678 | 4.678
105 |  | Internal diameter | [in] | 4.668 | 4.668 | 4.668 | 4.668 | 4.668 | 4.668
106 |  | Volumetric specific heat of the material | [J/(K*m³)] | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000
107 | Q Concentric wires | Thermal capacitance | [J/m.K] | 6.2441 | 6.2441 | 6.2441 | 6.2441 | 6.2441 | 6.2441
108 |  | Thermal capacitance equation
109 |  | Number of armour wires |  | 40 | 40 | 40 | 40 | 40 | 40
110 |  | Mean diameter of armour wire | [in] | 0.05076 | 0.05076 | 0.05076 | 0.05076 | 0.05076 | 0.05076
111 |  | Length of lay | [in] | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937
112 |  | Mean diameter of armour | [in] | 4.7288 | 4.7288 | 4.7288 | 4.7288 | 4.7288 | 4.7288
113 |  | Wire Shape is half-circle |  | 0 | 0 | 0 | 0 | 0 | 0
114 | Q Jacket | Thermal capacitance | [J/m.K] | 8467.1389 | 8467.1389 | 8467.1389 | 8467.1389 | 8467.1389 | 8467.1389
115 |  | Thermal capacitance equation
116 |  | External diameter | [in] | 5.4595 | 5.4595 | 5.4595 | 5.4595 | 5.4595 | 5.4595
117 |  | Internal diameter | [in] | 4.7795 | 4.7795 | 4.7795 | 4.7795 | 4.7795 | 4.7795
118 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
Ampacity
119 | T₄ | Total external thermal resistance | [K.m/W] | 1.9047 | 2.1023 | 2.2261 | 2.2254 | 2.1023 | 1.9046
Total external thermal resistance Equation
120 | I | Cable core ampacity | [A] | 1288 | 1288 | 1288 | 1288 | 1288 | 1288
Cable core ampacity Equation

## Short Circuit
Cable Short Circuit
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | Case 3 Duct Bank 3 ft 2 ft sep
Date: |  | 1/8/2026 12:34:43 PM
Symbol | Description |  | Unit | Circuit No. 1
| Cable Equipment ID |  |  | CAYUGA 230KV 5000 KCMIL
|  |  |  | Conductor | [5 empty] | Sheath | [5 empty] | Concentric neutral/Skid wires
|  |  |  | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2535.636 | 2535.636 | 2535.636 | 2535.636 | 2535.636 | 2535.636 | 47.3569 | 47.3569 | 47.3569 | 47.3569 | 47.3569 | 47.3569 | 52.2225 | 52.2225 | 52.2225 | 52.2225 | 52.2225 | 52.2225
θi | Initial Temperature |  | [°C] | 80.6159 | 86.7055 | 88.4009 | 88.4046 | 86.7081 | 80.6224 | 73.4022 | 79.4037 | 81.0763 | 81.08 | 79.4063 | 73.4087 | 73.4022 | 79.4037 | 81.0763 | 81.08 | 79.4063 | 73.4087
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 250 | 250 | 250 | 250 | 250 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1186776.475 | 1160072.7304 | 1152619.6511 | 1152603.4968 | 1160061.1505 | 1186747.7773 | 15928.6594 | 15220.8979 | 15020.1931 | 15019.7574 | 15220.5891 | 15927.9057 | 17565.2361 | 16784.7563 | 16563.4303 | 16562.9497 | 16784.4157 | 17564.4051
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1188604.3295 | 1161859.4562 | 1154394.8978 | 1154378.7186 | 1161847.8584 | 1188575.5876 | 19806.2678 | 18926.2117 | 18676.6482 | 18676.1063 | 18925.8277 | 19805.3307 | 18004.7337 | 17204.7255 | 16977.8618 | 16977.3692 | 17204.3765 | 18003.8818