## General Su...- CAYUGA 230 KV-33
General Summary Report
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | CAYUGA 230 KV HDD soil 90
Date: |  | 1/8/2026 1:59:22 PM
Simulation Data
Installation type: |  | Multiple Ductbanks
Steady State Option |  | Temperature
Ambient temperature [°C] |  | 14.2
Native Soil Thermal Resistivity [K.m/W] |  | 0.9
Consider Non-Isothermal Earth Surface |  | No
Consider effect of soil dry out |  | No
Consider Electrical interaction between circuits |  | No
Induced current in metallic layers as a fraction of conductor current (applied to all single phase circuits) [A] |  | 0
Installation Type:Multiple Ductbanks/Backfills
Ambient Soil Temperature at Installation Depth [°C] |  | 14.2
Native Soil Thermal Resistivity [K.m/W] |  | 0.9
Consider Non-Isothermal Earth Surface |  | No
Layer Name |  | X [ft] | Y [ft] | Width [ft] | Height [ft] | Thermal Resistivity [K.m/W]
NSTD DB1 |  | 15 | 29.0834 | 1.9709 | 1.9709 | 1.5
NSTD DB2 |  | -15 | 29.0834 | 1.9709 | 1.9709 | 1.5
General Cable Information
Cable ID |  | Number of Cores | Conductor Construction | Voltage [kV] | Conductor Area [mm²] | Cable Overall Diameter [in] | Maximum Steady-State Conductor Temperature [ºC] | Maximum Emergency Conductor Temperature [ºC]
CAYUGA 230KV 5000 KCMIL |  | Single Core | 6 Segments | 230 | 2535.636 | 5.4595 | 90 | 110
Detailed Cable Information
Cable ID |  | Conductor | Insulation | Sheath / Tape | Concentric Wires | Filler | Armour | Jacket / Armour Serving
CAYUGA 230KV 5000 KCMIL |  | Copper | XLPE Unfilled | Copper | Copper | n/a | n/a | Polyethylene
General Input Data
Cable | Cable ID | Circuit No. | Phase | Fq [Hz] | X [ft] | Y [ft] | DLF [p.u.] | Sheath / Shield Bonding
Cable Index Number | Cable Equipment ID | Circuit No. | Cable Phase | Operating Frequency | X coordinate | Y coordinate | Daily Load Factor | Bonding Type
1 | CAYUGA 230KV 5000 KCMIL | 1 | A | 60 | -15.3561 | 29.7485 | 1 | 1 Conductor 1 Point Bonded Triangular
2 | CAYUGA 230KV 5000 KCMIL | 1 | B | 60 | -14.644 | 29.7485 | 1 | 1 Conductor 1 Point Bonded Triangular
3 | CAYUGA 230KV 5000 KCMIL | 1 | C | 60 | -15 | 29.1315 | 1 | 1 Conductor 1 Point Bonded Triangular
4 | CAYUGA 230KV 5000 KCMIL | 2 | A | 60 | 14.644 | 29.7485 | 1 | 1 Conductor 1 Point Bonded Triangular
5 | CAYUGA 230KV 5000 KCMIL | 2 | B | 60 | 15.3561 | 29.7485 | 1 | 1 Conductor 1 Point Bonded Triangular
6 | CAYUGA 230KV 5000 KCMIL | 2 | C | 60 | 15 | 29.1315 | 1 | 1 Conductor 1 Point Bonded Triangular
Ampacity and Temperatures
Cable | Cable ID | I [A] | θc [°C] | θs [°C] | θa [°C] | θsurf [°C] | θduct [°C] | θair / θcasing [°C]
Cable Index Number | Cable Equipment ID | Steady State Ampacity | Conductor temperature | Sheath/Shield temperature | Armour temperature | Cable surface temperature | Duct surface temperature | Mean air temperature in the tunnel / Casing surface temperature
1 | CAYUGA 230KV 5000 KCMIL | 1143 | 88.3151 | 81.7054 | n/a | 80.1317 | 71.9009 | n/a
2 | CAYUGA 230KV 5000 KCMIL | 1143 | 88.5783 | 81.9659 | n/a | 80.3917 | 72.1644 | n/a
3 | CAYUGA 230KV 5000 KCMIL | 1143 | 87.2772 | 80.6779 | n/a | 79.1063 | 70.8619 | n/a
4 | CAYUGA 230KV 5000 KCMIL | 1143 | 88.5625 | 81.9502 | n/a | 80.3761 | 72.1485 | n/a
5 | CAYUGA 230KV 5000 KCMIL | 1143 | 88.303 | 81.6934 | n/a | 80.1197 | 71.8888 | n/a
6 | CAYUGA 230KV 5000 KCMIL | 1143 | 87.2696 | 80.6704 | n/a | 79.0988 | 70.8543 | n/a
Electrical Resistances
Cable | Cable ID | R₀ [Ω/mile] | ys | yp | R [Ω/mile] | R's [Ω/mile] | R'w [Ω/mile] | R'a [Ω/mile]
Cable Index Number | Cable Equipment ID | DC Resistance of the conductor at 20°C | Skin Effect Factor | Proximity Effect Factor | AC Resistance of Conductor at Operating Temperature | DC Resistance of Sheath at Operating Temperature | DC Resistance of Concentric Wires at Operating Temperature | DC Resistance of Armor at Operating Temperature
1 | CAYUGA 230KV 5000 KCMIL | 0.011162 | 0.57048 | 0.040062 | 0.022802 | 0.72799 | 24.9192 | n/a
2 | CAYUGA 230KV 5000 KCMIL | 0.011162 | 0.56988 | 0.040028 | 0.022812 | 0.72859 | 24.9397 | n/a
3 | CAYUGA 230KV 5000 KCMIL | 0.011162 | 0.57286 | 0.040196 | 0.022765 | 0.72562 | 24.8382 | n/a
4 | CAYUGA 230KV 5000 KCMIL | 0.011162 | 0.56991 | 0.04003 | 0.022811 | 0.72855 | 24.9385 | n/a
5 | CAYUGA 230KV 5000 KCMIL | 0.011162 | 0.57051 | 0.040063 | 0.022802 | 0.72796 | 24.9182 | n/a
6 | CAYUGA 230KV 5000 KCMIL | 0.011162 | 0.57288 | 0.040196 | 0.022764 | 0.72561 | 24.8376 | n/a
Thermal Resistances
Cable | Cable ID | T₁ [K.m/W] | T₂ [K.m/W] | T₃ [K.m/W] | T₄' [K.m/W] | T₄'' [K.m/W] | T₄''' [K.m/W] | T₄ [K.m/W]
Cable Index Number | Cable Equipment ID | Thermal resistance of insulation | Thermal resistance of bedding | Thermal resistance of outer covering | Thermal resistance inside the duct | Thermal resistance of the duct | Thermal resistance of the external medium | Total external thermal resistance
1 | CAYUGA 230KV 5000 KCMIL | 0.34068 | 0 | 0.074098 | 0.20045 | 0.18709 | 2.7169 | 3.1044
2 | CAYUGA 230KV 5000 KCMIL | 0.34068 | 0 | 0.074098 | 0.20017 | 0.18709 | 2.7284 | 3.1156
3 | CAYUGA 230KV 5000 KCMIL | 0.34068 | 0 | 0.074098 | 0.2016 | 0.18709 | 2.6714 | 3.0601
4 | CAYUGA 230KV 5000 KCMIL | 0.34068 | 0 | 0.074098 | 0.20018 | 0.18709 | 2.7277 | 3.115
5 | CAYUGA 230KV 5000 KCMIL | 0.34068 | 0 | 0.074098 | 0.20047 | 0.18709 | 2.7163 | 3.1039
6 | CAYUGA 230KV 5000 KCMIL | 0.34068 | 0 | 0.074098 | 0.20161 | 0.18709 | 2.6711 | 3.0598
Losses
Cable | Cable ID | Wc [W/ft] | Wd [W/ft] | Ws [W/ft] | Wa [W/ft] | Wt [W/ft] | ƛ₁ | ƛ₂
Cable Index Number | Cable Equipment ID | Conductor Losses | Dielectric Losses | Metallic Screen Losses | Armor/Pipe Losses | Total Losses | Screen Loss Factor | Armour Loss Factor + Pipe Loss Factor
1 | CAYUGA 230KV 5000 KCMIL | 5.6421 | 0.54297 | 0.28835 | 0 | 6.4734 | 0.051107 | 0
2 | CAYUGA 230KV 5000 KCMIL | 5.6444 | 0.54297 | 0.28812 | 0 | 6.4755 | 0.051044 | 0
3 | CAYUGA 230KV 5000 KCMIL | 5.6327 | 0.54297 | 0.28927 | 0 | 6.465 | 0.051356 | 0
4 | CAYUGA 230KV 5000 KCMIL | 5.6443 | 0.54297 | 0.28813 | 0 | 6.4754 | 0.051048 | 0
5 | CAYUGA 230KV 5000 KCMIL | 5.642 | 0.54297 | 0.28836 | 0 | 6.4733 | 0.05111 | 0
6 | CAYUGA 230KV 5000 KCMIL | 5.6326 | 0.54297 | 0.28928 | 0 | 6.4649 | 0.051358 | 0
Complementary Information
Cable | Cable ID | Δθint [°C] | [A] | [µF/mile] | [Ω] | [Ω/mile] | [Ω/mile] | [V/A/mile]
Cable Index Number | Cable Equipment ID | Temperature rise due to surrounding heat sources | Induced current on Metallic Screen | Cable Capacitance | Surge Impedance | Reactance of Conductor | Reactance of Metallic Sheath | Voltage drop for Three Phase System
1 | CAYUGA 230KV 5000 KCMIL | 39.419 | 0 | 0.4313 | 40.3405 | 0.26458 | 0.15664 | 0.039495
2 | CAYUGA 230KV 5000 KCMIL | 39.6736 | 0 | 0.4313 | 40.3405 | 0.26458 | 0.15664 | 0.039511
3 | CAYUGA 230KV 5000 KCMIL | 36.6851 | 0 | 0.4313 | 40.3405 | 0.26458 | 0.15664 | 0.039429
4 | CAYUGA 230KV 5000 KCMIL | 39.6743 | 0 | 0.4313 | 40.3405 | 0.26458 | 0.15664 | 0.03951
5 | CAYUGA 230KV 5000 KCMIL | 39.4166 | 0 | 0.4313 | 40.3405 | 0.26458 | 0.15664 | 0.039494
6 | CAYUGA 230KV 5000 KCMIL | 36.6831 | 0 | 0.4313 | 40.3405 | 0.26458 | 0.15664 | 0.039429

## Study Summary
Study Summary
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | CAYUGA 230 KV HDD soil 90
Date: |  | 1/8/2026 1:59:22 PM
General Simulation Data
Steady State Option | [8 empty] | Temperature
Consider Electrical interaction between circuits | [8 empty] | No
Induced currents in metallic layers as a fraction of conductor current (applied to all single phase circuits) : | [8 empty] | 0
Conductor Resistances Computation Option: | [8 empty] | IEC-228
Standard Settings Options
General guidance | [8 empty] | Custom
Factor on RAC due to magnetic armour | [8 empty] | CIGREGuidance
Factor on RAC due to magnetic duct | [8 empty] | CIGREGuidance
Factor on ƛ₁ due to magnetic armour | [8 empty] | CYMCAPGuidance
Factor on ƛ₁ due to magnetic duct | [8 empty] | CIGREGuidance
Factor on ƛ₂ due to ƛ'₁ | [8 empty] | CYMCAPGuidance
ƛ''₁ computation | [8 empty] | CIGREGuidance
ƛ₂pipe computation | [8 empty] | CYMCAPGuidance
Wd computation | [8 empty] | CIGREGuidance
T₂ computation | [8 empty] | CIGREGuidance
T₄ computation | [8 empty] | CYMCAPGuidance
Installation Type:Multiple Ductbanks/Backfills
Ambient Soil Temperature at Installation Depth [°C] | [8 empty] | 14.2
Native Soil Thermal Resistivity [K.m/W] | [8 empty] | 0.9
Consider Non-Isothermal Earth Surface | [8 empty] | No
Layer Name |  | X [ft] | Y [ft] | Width [ft] | Height [ft] | Thermal Resistivity [K.m/W]
NSTD DB1 |  | 15 | 29.0834 | 1.9709 | 1.9709 | 1.5
NSTD DB2 |  | -15 | 29.0834 | 1.9709 | 1.9709 | 1.5
Results Summary
Cable No. | Cable ID | Circuit No. | Feeder ID | Cable Phase | Cable Frequency | Daily Load Factor | X coordinate [ft] | Y coordinate [ft] | Conductor temperature [°C] | Ampacity [A]
1 | CAYUGA 230KV 5000 KCMIL | 1 |  | A | 60 | 1 | -15.3561 | 29.7485 | 88.3151 | 1143
2 | CAYUGA 230KV 5000 KCMIL | 1 |  | B | 60 | 1 | -14.644 | 29.7485 | 88.5783 | 1143
3 | CAYUGA 230KV 5000 KCMIL | 1 |  | C | 60 | 1 | -15 | 29.1315 | 87.2772 | 1143
4 | CAYUGA 230KV 5000 KCMIL | 2 |  | A | 60 | 1 | 14.644 | 29.7485 | 88.5625 | 1143
5 | CAYUGA 230KV 5000 KCMIL | 2 |  | B | 60 | 1 | 15.3561 | 29.7485 | 88.303 | 1143
6 | CAYUGA 230KV 5000 KCMIL | 2 |  | C | 60 | 1 | 15 | 29.1315 | 87.2696 | 1143

## Steady State Summary
Steady State Summary
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | CAYUGA 230 KV HDD soil 90
Date: |  | 1/8/2026 1:59:22 PM
Simulation Data
Installation type: |  | Multiple Ductbanks
Steady State Option |  | Temperature
Ambient temperature [°C] |  | 14.2
Native Soil Thermal Resistivity [K.m/W] |  | 0.9
Consider Non-Isothermal Earth Surface |  | No
Consider effect of soil dry out |  | No
Consider Electrical interaction between circuits |  | No
Induced current in metallic layers as a fraction of conductor current (applied to all single phase circuits) [A] |  | 0
Variable | Description |  | Unit | Cables
Cable No. | Cable Index Number |  |  | 1 | 2 | 3 | 4 | 5 | 6
General Input Data
Cable ID | Cable Equipment ID |  |  | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL
Circuit No. | Circuit No. |  |  | 1 | 1 | 1 | 2 | 2 | 2
Phase | Cable Phase |  |  | A | B | C | A | B | C
Fq | Operating Frequency |  | [Hz] | 60 | 60 | 60 | 60 | 60 | 60
x | X coordinate |  | [ft] | -15.3561 | -14.644 | -15 | 14.644 | 15.3561 | 15
y | Y coordinate |  | [ft] | 29.7485 | 29.7485 | 29.1315 | 29.7485 | 29.7485 | 29.1315
DLF | Daily Load Factor |  | [p.u.] | bar: Cables 1 to Cables 6
| Bonding Type |  |  | 1 Conductor 1 Point Bonded Triangular | 1 Conductor 1 Point Bonded Triangular | 1 Conductor 1 Point Bonded Triangular | 1 Conductor 1 Point Bonded Triangular | 1 Conductor 1 Point Bonded Triangular | 1 Conductor 1 Point Bonded Triangular
Ampacity
I | Steady State Ampacity |  | [A] | 1143 | 1143 | 1143 | 1143 | 1143 | 1143
I₀ | Steady State Ampacity without insulation temperature drop constraint |  | [A] | n/a | n/a | n/a | n/a | n/a | n/a
Temperatures
θc | Conductor temperature |  | [°C] | 88.3151 | 88.5783 | 87.2772 | 88.5625 | 88.303 | 87.2696
Δθins | Temperature drop across the insulation |  | [°C] | n/a | n/a | n/a | n/a | n/a | n/a
θs | Sheath/Shield temperature |  | [°C] | 81.7054 | 81.9659 | 80.6779 | 81.9502 | 81.6934 | 80.6704
θa | Armour temperature |  | [°C] | n/a | n/a | n/a | n/a | n/a | n/a
θsurf | Cable surface temperature |  | [°C] | 80.1317 | 80.3917 | 79.1063 | 80.3761 | 80.1197 | 79.0988
θduct | Duct surface temperature |  | [°C] | 71.9009 | 72.1644 | 70.8619 | 72.1485 | 71.8888 | 70.8543
Resistances
R₀ | DC Resistance of the conductor at 20°C |  | [Ω/mile] | 0.011162 | 0.011162 | 0.011162 | 0.011162 | 0.011162 | 0.011162
R | AC Resistance of the Conductor at Operating Temperature |  | [Ω/mile] | 0.022802 | 0.022812 | 0.022765 | 0.022811 | 0.022802 | 0.022764
ys | Skin Effect Factor |  |  | 0.57048 | 0.56988 | 0.57286 | 0.56991 | 0.57051 | 0.57288
yp | Proximity Effect Factor |  |  | 0.040062 | 0.040028 | 0.040196 | 0.04003 | 0.040063 | 0.040196
Losses
Wc | Conductor Losses |  | [W/ft] | 5.6421 | 5.6444 | 5.6327 | 5.6443 | 5.642 | 5.6326
Wd | Dielectric Losses |  | [W/ft] | 0.54297 | 0.54297 | 0.54297 | 0.54297 | 0.54297 | 0.54297
Ws | Metallic Screen Losses |  | [W/ft] | 0.28835 | 0.28812 | 0.28927 | 0.28813 | 0.28836 | 0.28928
Wa | Armor/Pipe Losses |  | [W/ft] | 0 | 0 | 0 | 0 | 0 | 0
Wt | Total Losses |  | [W/ft] | 6.4734 | 6.4755 | 6.465 | 6.4754 | 6.4733 | 6.4649
ƛ₁ | Screen Loss Factor |  |  | 0.051107 | 0.051044 | 0.051356 | 0.051048 | 0.05111 | 0.051358
ƛ₂ | Armour Loss Factor + Pipe Loss Factor |  |  | 0 | 0 | 0 | 0 | 0 | 0
Thermal resistances
T1 | Thermal Resistance Between Conductor and Screen |  | [K.m/W] | 0.34068 | 0.34068 | 0.34068 | 0.34068 | 0.34068 | 0.34068
T2 | Thermal Resistance Between Screen and Armour |  | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
T3 | Thermal Resistance of the Jacket/Pipe Coating |  | [K.m/W] | 0.074098 | 0.074098 | 0.074098 | 0.074098 | 0.074098 | 0.074098
T4 | Total external thermal resistance |  | [K.m/W] | 3.1044 | 3.1156 | 3.0601 | 3.115 | 3.1039 | 3.0598
Others
Δθint | Temperature rise due to surrounding heat sources |  | [°C] | 39.419 | 39.6736 | 36.6851 | 39.6743 | 39.4166 | 36.6831
| Induced Voltage (standing) on Sheath |  | [V/mile] | 182.3237 | 177.388 | 179.9347 | 177.388 | 182.3237 | 179.9347
| Induced Voltage angle on Sheath |  | [°] | -30.4145 | 89.5046 | -149.0926 | -29.5046 | 90.4145 | -150.9074
| Induced Voltage (standing) on Concentric Wires |  | [V/mile] | 180.6786 | 175.7429 | 178.2898 | 175.7429 | 180.6786 | 178.2898
| Induced Voltage angle on Concentric Wires |  | [°] | -30.4183 | 89.5 | -149.0842 | -29.5 | 90.4183 | -150.9158
| Induced current on Metallic Screen |  | [A] | 0 | 0 | 0 | 0 | 0 | 0

## Cable - CA...A 230KV 5000 KCMIL
Cables Report
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | CAYUGA 230 KV HDD soil 90
Date: |  | 1/8/2026 1:59:22 PM
No. | Description |  | Unit | 1
General Cable Information
1 | Cable Equipment ID |  |  | CAYUGA 230KV 5000 KCMIL
2 | Number of Cores |  |  | Single Core
3 | Voltage |  | [kV] | 230
4 | Conductor Area |  | [in²] | 3.9302
5 | Cable Overall Diameter |  | [in] | 5.4595
6 | Maximum Steady-State Conductor Temperature |  | [°C] | 90
7 | Maximum Emergency Conductor Temperature |  | [°C] | 110
Conductor
8 | Material |  |  | Copper
9 | Electrical Resistivity at 20°C |  | [µΩ.cm] | 1.7241
10 | Temperature Coefficient at 20°C |  | [1/K] | 0.00393
11 | Reciprocal of Temperature Coefficient of Resistance (BETA) |  | [K] | 234.4529
12 | Volumetric Specific Heat (SH) |  | [J/(K*cm³)] | 3.45
13 | Construction |  |  | 6 Segments
14 | Conductor Insulation System |  |  | Extruded
15 | Milliken Wires Construction |  |  | Bare Bidirectional Wires
16 | Ks (Skin Effect Coefficient) |  |  | 0.8
17 | Kp (Proximity Effect Coefficient) |  |  | 0.37
18 | Diameter |  | [in] | 2.48
Conductor Shield
19 | Thickness |  | [in] | 0.094
20 | Diameter |  | [in] | 2.668
Insulation
21 | Material |  |  | XLPE Unfilled
22 | Thermal Resistivity |  | [K.m/W] | 3.5
23 | Dielectric Loss Factor - ( tan delta ) |  |  | 0.001
24 | Relative Permittivity - ( epsilon ) |  |  | 2.5
25 | Specific Insulation Resistance Constant at 60°F - ( K ) |  | [㏁.1000ft] | 1858.0608
26 | Thickness |  | [in] | 0.906
27 | Diameter |  | [in] | 4.48
Insulation Screen
28 | Material |  |  | Semi Conducting Screen
29 | Thickness |  | [in] | 0.094
30 | Diameter |  | [in] | 4.668
Sheath
31 | Is Sheath Around Each Core? |  |  | n/a
32 | Material |  |  | Copper
33 | Electrical Resistivity at 20°C |  | [µΩ.cm] | 1.7241
34 | Temperature Coefficient at 20°C |  | [1/K] | 0.00393
35 | Reciprocal of Temperature Coefficient of Resistance (BETA) |  | [K] | 234.5
36 | Volumetric Specific Heat (SH) |  | [J/(K*cm³)] | 3.45
37 | Corrugation Type |  |  | Non Corrugated
38 | Thickness |  | [in] | 0.005
39 | Diameter |  | [in] | 4.678
Concentric neutral/Skid wires
40 | Are Concentric Neutral Wires Around Each Core? |  |  | n/a
41 | Material |  |  | Copper
42 | Electrical Resistivity at 20°C |  | [µΩ.cm] | 1.7241
43 | Temperature Coefficient at 20°C |  | [1/K] | 0.00393
44 | Reciprocal of Temperature Coefficient of Resistance (BETA) |  | [K] | 234.5
45 | Volumetric Specific Heat (SH) |  | [J/(K*cm³)] | 3.45
46 | Wire Type |  |  | Round Wires
47 | Length of Lay |  | [in] | 0.3937
48 | Number of Wires |  |  | 40
49 | Wire Gauge |  |  | 16
50 | Thickness |  | [in] | 0.05076
51 | Diameter |  | [in] | 4.7795
Jacket
52 | Material |  |  | Polyethylene
53 | Thermal Resistivity |  | [K.m/W] | 3.5
54 | Thickness |  | [in] | 0.34
55 | Diameter |  | [in] | 5.4595
No. | Description |  | Unit | 1
Specific Installation Data
56 | Cable Equipment ID |  |  | CAYUGA 230KV 5000 KCMIL
57 | Cable Frequency |  | [Hz] | 60
58 | Sheath / Shield Bonding |  |  | 1 Conductor 1 Point Bonded Triangular
59 | Loss Factor Constant (ALOS) |  |  | 0.3
60 | Spacing Between Cables in Section |  |  | n/a
61 | Conduit construction |  |  | PVC Duct in Concrete
62 | Conduit material thermal resistivity |  | [K.m/W] | 6
63 | Conduit filling material |  |  | Air
64 | Inner diameter of the conduit |  | [in] | 6.963
65 | Outer diameter of the conduit |  | [in] | 8.47
Cable ID : CAYUGA 230KV 5000 KCMIL
Cable Title |  | CAYUGA 230KV 5000 kcmil

## Impedances
Cable Impedances & Admittances
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | CAYUGA 230 KV HDD soil 90
Date: |  | 1/8/2026 1:59:22 PM
Earth Resistivity: [Ω.m] |  | 100
Frequency: [Hz] |  | 60
Temperature
|  |  | Circuit 1 | [8 empty] | Circuit 2
|  |  | Conductor |  |  | Sheath |  |  | Concentric neutral/Skid wires |  |  | Conductor |  |  | Sheath |  |  | Concentric neutral/Skid wires
|  | Phase | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C
| Temperature | [°C] | 88.3151 | 88.5783 | 87.2772 | 81.7054 | 81.9659 | 80.6779 | 81.7054 | 81.9659 | 80.6779 | 88.5625 | 88.303 | 87.2696 | 81.9502 | 81.6934 | 80.6704 | 81.9502 | 81.6934 | 80.6704
R_Primitive [Ω/mile]
|  |  | Circuit No. 1 |  |  | Circuit No. 2 |  |  | Circuit No. 1 |  |  | Circuit No. 2 |  |  | Circuit No. 1 |  |  | Circuit No. 2
|  |  | Conductor | [5 empty] | Sheath | [5 empty] | Concentric neutral/Skid wires
|  | Phase | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C
Circuit No. 1 | Conductor | A | 0.1181 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.11811 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.11811 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 2 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.11811 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11811 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11811 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 1 | Sheath | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.82329 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.82389 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.82389 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 2 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.82389 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.82389 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.82389 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 1 | Concentric neutral Skid wires | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 25.0145 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 25.035 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 25.035 | 0.095302 | 0.095302 | 0.095302
Circuit No. 2 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 25.035 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 25.035 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 25.035
X Primitive [Ω/mile]
|  |  | Circuit No. 1 |  |  | Circuit No. 2 |  |  | Circuit No. 1 |  |  | Circuit No. 2 |  |  | Circuit No. 1 |  |  | Circuit No. 2
|  |  | Conductor | [5 empty] | Sheath | [5 empty] | Concentric neutral/Skid wires
|  | Phase | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C
Circuit No. 1 | Conductor | A | 1.2685 | 1.004 | 1.0038 | 0.55001 | 0.54717 | 0.54856 | 1.1613 | 1.004 | 1.0038 | 0.55001 | 0.54717 | 0.54856 | 1.1598 | 1.004 | 1.0038 | 0.55001 | 0.54717 | 0.54856
|  | B | 1.004 | 1.2685 | 1.0041 | 0.55292 | 0.55001 | 0.55144 | 1.004 | 1.1613 | 1.0041 | 0.55292 | 0.55001 | 0.55144 | 1.004 | 1.1598 | 1.0041 | 0.55292 | 0.55001 | 0.55144
|  | C | 1.0038 | 1.0041 | 1.2685 | 0.55144 | 0.54856 | 0.55002 | 1.0038 | 1.0041 | 1.1613 | 0.55144 | 0.54856 | 0.55002 | 1.0038 | 1.0041 | 1.1598 | 0.55144 | 0.54856 | 0.55002
Circuit No. 2 |  | A | 0.55001 | 0.55292 | 0.55144 | 1.2685 | 1.004 | 1.0041 | 0.55001 | 0.55292 | 0.55144 | 1.1613 | 1.004 | 1.0041 | 0.55001 | 0.55292 | 0.55144 | 1.1598 | 1.004 | 1.0041
|  | B | 0.54717 | 0.55001 | 0.54856 | 1.004 | 1.2685 | 1.0038 | 0.54717 | 0.55001 | 0.54856 | 1.004 | 1.1613 | 1.0038 | 0.54717 | 0.55001 | 0.54856 | 1.004 | 1.1598 | 1.0038
|  | C | 0.54856 | 0.55144 | 0.55002 | 1.0041 | 1.0038 | 1.2685 | 0.54856 | 0.55144 | 0.55002 | 1.0041 | 1.0038 | 1.1613 | 0.54856 | 0.55144 | 0.55002 | 1.0041 | 1.0038 | 1.1598
Circuit No. 1 | Sheath | A | 1.1613 | 1.004 | 1.0038 | 0.55001 | 0.54717 | 0.54856 | 1.1613 | 1.004 | 1.0038 | 0.55001 | 0.54717 | 0.54856 | 1.1598 | 1.004 | 1.0038 | 0.55001 | 0.54717 | 0.54856
|  | B | 1.004 | 1.1613 | 1.0041 | 0.55292 | 0.55001 | 0.55144 | 1.004 | 1.1613 | 1.0041 | 0.55292 | 0.55001 | 0.55144 | 1.004 | 1.1598 | 1.0041 | 0.55292 | 0.55001 | 0.55144
|  | C | 1.0038 | 1.0041 | 1.1613 | 0.55144 | 0.54856 | 0.55002 | 1.0038 | 1.0041 | 1.1613 | 0.55144 | 0.54856 | 0.55002 | 1.0038 | 1.0041 | 1.1598 | 0.55144 | 0.54856 | 0.55002
Circuit No. 2 |  | A | 0.55001 | 0.55292 | 0.55144 | 1.1613 | 1.004 | 1.0041 | 0.55001 | 0.55292 | 0.55144 | 1.1613 | 1.004 | 1.0041 | 0.55001 | 0.55292 | 0.55144 | 1.1598 | 1.004 | 1.0041
|  | B | 0.54717 | 0.55001 | 0.54856 | 1.004 | 1.1613 | 1.0038 | 0.54717 | 0.55001 | 0.54856 | 1.004 | 1.1613 | 1.0038 | 0.54717 | 0.55001 | 0.54856 | 1.004 | 1.1598 | 1.0038
|  | C | 0.54856 | 0.55144 | 0.55002 | 1.0041 | 1.0038 | 1.1613 | 0.54856 | 0.55144 | 0.55002 | 1.0041 | 1.0038 | 1.1613 | 0.54856 | 0.55144 | 0.55002 | 1.0041 | 1.0038 | 1.1598
Circuit No. 1 | Concentric neutral Skid wires | A | 1.1598 | 1.004 | 1.0038 | 0.55001 | 0.54717 | 0.54856 | 1.1598 | 1.004 | 1.0038 | 0.55001 | 0.54717 | 0.54856 | 1.1632 | 1.004 | 1.0038 | 0.55001 | 0.54717 | 0.54856
|  | B | 1.004 | 1.1598 | 1.0041 | 0.55292 | 0.55001 | 0.55144 | 1.004 | 1.1598 | 1.0041 | 0.55292 | 0.55001 | 0.55144 | 1.004 | 1.1632 | 1.0041 | 0.55292 | 0.55001 | 0.55144
|  | C | 1.0038 | 1.0041 | 1.1598 | 0.55144 | 0.54856 | 0.55002 | 1.0038 | 1.0041 | 1.1598 | 0.55144 | 0.54856 | 0.55002 | 1.0038 | 1.0041 | 1.1632 | 0.55144 | 0.54856 | 0.55002
Circuit No. 2 |  | A | 0.55001 | 0.55292 | 0.55144 | 1.1598 | 1.004 | 1.0041 | 0.55001 | 0.55292 | 0.55144 | 1.1598 | 1.004 | 1.0041 | 0.55001 | 0.55292 | 0.55144 | 1.1632 | 1.004 | 1.0041
|  | B | 0.54717 | 0.55001 | 0.54856 | 1.004 | 1.1598 | 1.0038 | 0.54717 | 0.55001 | 0.54856 | 1.004 | 1.1598 | 1.0038 | 0.54717 | 0.55001 | 0.54856 | 1.004 | 1.1632 | 1.0038
|  | C | 0.54856 | 0.55144 | 0.55002 | 1.0041 | 1.0038 | 1.1598 | 0.54856 | 0.55144 | 0.55002 | 1.0041 | 1.0038 | 1.1598 | 0.54856 | 0.55144 | 0.55002 | 1.0041 | 1.0038 | 1.1632
R Bonding [Ω/mile]
|  |  | Circuit No. 1 |  |  | Circuit No. 2
Conductor
|  | Phase | A | B | C | A | B | C
Circuit No. 1 | Conductor | A | 0.1181 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.11811 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.11811 | 0.095302 | 0.095302 | 0.095302
Circuit No. 2 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.11811 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11811 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11811
X Bonding [Ω/mile]
|  |  | Circuit No. 1 |  |  | Circuit No. 2
Conductor
|  | Phase | A | B | C | A | B | C
Circuit No. 1 | Conductor | A | 1.2685 | 1.004 | 1.0038 | 0.55001 | 0.54717 | 0.54856
|  | B | 1.004 | 1.2685 | 1.0041 | 0.55292 | 0.55001 | 0.55144
|  | C | 1.0038 | 1.0041 | 1.2685 | 0.55144 | 0.54856 | 0.55002
Circuit No. 2 |  | A | 0.55001 | 0.55292 | 0.55144 | 1.2685 | 1.004 | 1.0041
|  | B | 0.54717 | 0.55001 | 0.54856 | 1.004 | 1.2685 | 1.0038
|  | C | 0.54856 | 0.55144 | 0.55002 | 1.0041 | 1.0038 | 1.2685
R Phase [Ω/mile]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | A | B | C | A | B | C
Circuit No. 1 | A | 0.1181 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.11811 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| C | 0.095302 | 0.095302 | 0.11811 | 0.095302 | 0.095302 | 0.095302
Circuit No. 2 | A | 0.095302 | 0.095302 | 0.095302 | 0.11811 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11811 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11811
X Phase [Ω/mile]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | A | B | C | A | B | C
Circuit No. 1 | A | 1.2685 | 1.004 | 1.0038 | 0.55001 | 0.54717 | 0.54856
| B | 1.004 | 1.2685 | 1.0041 | 0.55292 | 0.55001 | 0.55144
| C | 1.0038 | 1.0041 | 1.2685 | 0.55144 | 0.54856 | 0.55002
Circuit No. 2 | A | 0.55001 | 0.55292 | 0.55144 | 1.2685 | 1.004 | 1.0041
| B | 0.54717 | 0.55001 | 0.54856 | 1.004 | 1.2685 | 1.0038
| C | 0.54856 | 0.55144 | 0.55002 | 1.0041 | 1.0038 | 1.2685
R Circuit [Ω/mile]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | A | B | C | A | B | C
Circuit No. 1 | A | 0.1181 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.11811 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| C | 0.095302 | 0.095302 | 0.11811 | 0.095302 | 0.095302 | 0.095302
Circuit No. 2 | A | 0.095302 | 0.095302 | 0.095302 | 0.11811 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11811 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11811
X Circuit [Ω/mile]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | A | B | C | A | B | C
Circuit No. 1 | A | 1.2685 | 1.004 | 1.0038 | 0.55001 | 0.54717 | 0.54856
| B | 1.004 | 1.2685 | 1.0041 | 0.55292 | 0.55001 | 0.55144
| C | 1.0038 | 1.0041 | 1.2685 | 0.55144 | 0.54856 | 0.55002
Circuit No. 2 | A | 0.55001 | 0.55292 | 0.55144 | 1.2685 | 1.004 | 1.0041
| B | 0.54717 | 0.55001 | 0.54856 | 1.004 | 1.2685 | 1.0038
| C | 0.54856 | 0.55144 | 0.55002 | 1.0041 | 1.0038 | 1.2685
R Sequence [Ω/mile]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | 0 | 1 | 2 | 0 | 1 | 2
Circuit No. 1 | 0 | 0.30871 | 4.7e-05 | -5.4e-05 | 0.28591 | -0.001238 | 0.001238
| 1 | -5.4e-05 | 0.022809 | -0.000104 | -0.001256 | -1e-06 | -3e-05
| 2 | 4.7e-05 | 9.8e-05 | 0.022809 | 0.001256 | 3e-05 | 1e-06
Circuit No. 2 | 0 | 0.28591 | 0.001256 | -0.001256 | 0.30872 | -3e-05 | 3e-05
| 1 | 0.001238 | 1e-06 | -3e-05 | 3e-05 | 0.022812 | 6e-05
| 2 | -0.001238 | 3e-05 | -1e-06 | -3e-05 | -6e-05 | 0.022812
X Sequence [Ω/mile]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | 0 | 1 | 2 | 0 | 1 | 2
Circuit No. 1 | 0 | 3.2763 | -6.4e-05 | -6.4e-05 | 1.65 | 0.002165 | 0.002165
| 1 | -6.4e-05 | 0.26452 | 0.000128 | -0.002154 | 0 | -1.7e-05
| 2 | -6.4e-05 | 0.000128 | 0.26452 | -0.002154 | -1.7e-05 | 0
Circuit No. 2 | 0 | 1.65 | -0.002154 | -0.002154 | 3.2763 | 7.6e-05 | 7.6e-05
| 1 | 0.002165 | 0 | -1.7e-05 | 7.6e-05 | 0.26452 | -0.000151
| 2 | 0.002165 | -1.7e-05 | 0 | 7.6e-05 | -0.000151 | 0.26452
R Sequence/R1
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | 0 | 1 | 2 | 0 | 1 | 2
Circuit No. 1 | 0 | 13.533 | 0.002074 | 0.002355 | 12.5331 | 0.054258 | 0.054258
| 1 | 0.002355 | 0.99986 | 0.004569 | 0.055052 | 3.7e-05 | 0.001298
| 2 | 0.002074 | 0.004288 | 0.99986 | 0.055052 | 0.001298 | 3.7e-05
Circuit No. 2 | 0 | 12.5331 | 0.055052 | 0.055052 | 13.5331 | 0.001322 | 0.001322
| 1 | 0.054258 | 3.7e-05 | 0.001298 | 0.001322 | 1 | 0.002644
| 2 | 0.054258 | 0.001298 | 3.7e-05 | 0.001322 | 0.002644 | 1
X Sequence/X1
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | 0 | 1 | 2 | 0 | 1 | 2
Circuit No. 1 | 0 | 12.3858 | 0.000242 | 0.000242 | 6.2378 | 0.008184 | 0.008184
| 1 | 0.000242 | 1 | 0.000484 | 0.008144 | 0 | 6.5e-05
| 2 | 0.000242 | 0.000484 | 1 | 0.008144 | 6.5e-05 | 0
Circuit No. 2 | 0 | 6.2378 | 0.008144 | 0.008144 | 12.3858 | 0.000286 | 0.000286
| 1 | 0.008184 | 0 | 6.5e-05 | 0.000286 | 1 | 0.000573
| 2 | 0.008184 | 6.5e-05 | 0 | 0.000286 | 0.000573 | 1
Symmetrical Components [Ω/mile] | bar: Circuit No. 1 0 to Circuit No. 1 2
Circuit | Z0 | Circuit No. 1 0: Z1; Circuit No. 1 1: Z2; Circuit No. 1 2: ZOM(1,2)
1 | 0.308713 + j 3.276324 | Circuit No. 1 0: 0.022809 + j 0.264522; Circuit No. 1 1: 0.022809 + j 0.264522; Circuit No. 1 2: 0.285905 + j 1.650044
2 | 0.308717 + j 3.276324 | Circuit No. 1 0: 0.022812 + j 0.264522; Circuit No. 1 1: 0.022812 + j 0.264522; Circuit No. 1 2: 0.285905 + j 1.650044
Y Primitive [µS/mile] | bar: Circuit No. 1 0 to Circuit No. 2 0
Circuit No. 1 |  | Circuit No. 1 1: Circuit No. 2
A | B | C | A | B | C
0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781
Y Circuit [µS/mile] | bar: Circuit No. 1 0 to Circuit No. 2 0
Circuit No. 1 |  | Circuit No. 1 1: Circuit No. 2
A | B | C | A | B | C
0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781
Y Sequence [µS/mile] | bar: Circuit No. 1 0 to Circuit No. 2 0
Circuit No. 1 |  | Circuit No. 1 1: Circuit No. 2
0 | 1 | 2 | 0 | 1 | 2
0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781

## Electrical Parameters
Electrical Parameters
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | CAYUGA 230 KV HDD soil 90
Date: |  | 1/8/2026 1:59:22 PM
No. | Description |  | Unit | Cable No.1 | Cable No.2 | Cable No.3 | Cable No.4 | Cable No.5 | Cable No.6
1 | Cable Equipment ID |  |  | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL
Resistances
2 | DC Resistance of the conductor at 20°C |  | [Ω/mile] | 0.011162 | 0.011162 | 0.011162 | 0.011162 | 0.011162 | 0.011162
DC Resistance of the conductor at 20°C Equation
3 | DC Resistance of Conductor at Operating Temperature |  | [Ω/mile] | 0.014158 | 0.01417 | 0.014113 | 0.014169 | 0.014158 | 0.014112
DC Resistance of Conductor at Operating Temperature Equation
4 | AC Resistance of Conductor at 20°C |  | [Ω/mile] | 0.020015 | 0.020015 | 0.020015 | 0.020015 | 0.020015 | 0.020015
5 | AC Resistance of Conductor at Operating Temperature |  | [Ω/mile] | 0.022802 | 0.022812 | 0.022765 | 0.022811 | 0.022802 | 0.022764
AC Resistance of Conductor at Operating Temperature Equation
6 | DC Resistance of Sheath at 20°C |  | [Ω/mile] | 0.58591 | 0.58591 | 0.58591 | 0.58591 | 0.58591 | 0.58591
7 | DC Resistance of Sheath at Operating Temperature |  | [Ω/mile] | 0.72799 | 0.72859 | 0.72562 | 0.72855 | 0.72796 | 0.72561
DC Resistance of Sheath at Operating Temperature Equation
8 | DC Resistance of Concentric Wires at 20°C |  | [Ω/mile] | 20.0557 | 20.0557 | 20.0557 | 20.0557 | 20.0557 | 20.0557
9 | DC Resistance of Concentric Wires at Operating Temperature |  | [Ω/mile] | 24.9192 | 24.9397 | 24.8382 | 24.9385 | 24.9182 | 24.8376
DC Resistance of Concentric Wires at Operating Temperature Equation
Losses
10 | Conductor Losses |  | [W/ft] | 5.6421 | 5.6444 | 5.6327 | 5.6443 | 5.642 | 5.6326
Conductor Losses Equation
11 | Dielectric Losses |  | [W/ft] | 0.54297 | 0.54297 | 0.54297 | 0.54297 | 0.54297 | 0.54297
Dielectric Losses Equation
12 | Metallic Screen Losses |  | [W/ft] | 0.28835 | 0.28812 | 0.28927 | 0.28813 | 0.28836 | 0.28928
Metallic Screen Losses Equation
13 | Armor/Pipe Losses |  | [W/ft] | 0 | 0 | 0 | 0 | 0 | 0
Armor/Pipe Losses Equation
14 | Total Losses |  | [W/ft] | 6.4734 | 6.4755 | 6.465 | 6.4754 | 6.4733 | 6.4649
Total Losses Equation
Capacitance, Inductance, Impedance
15 | Capacitance |  | [µF/mile] | 0.4313 | 0.4313 | 0.4313 | 0.4313 | 0.4313 | 0.4313
Capacitance Equation
16 | Inductance of Conductor |  | [mH/mile] | 0.70181 | 0.70181 | 0.70181 | 0.70181 | 0.70181 | 0.70181
Inductance of Conductor Equation
17 | Reactance of Conductor |  | [Ω/mile] | 0.26458 | 0.26458 | 0.26458 | 0.26458 | 0.26458 | 0.26458
Reactance of Conductor Equation
18 | Inductance of Metallic Sheath |  | [mH/mile] | 0.41551 | 0.41551 | 0.41551 | 0.41551 | 0.41551 | 0.41551
Inductance of Metallic Sheath Equation
19 | Reactance of Metallic Sheath |  | [Ω/mile] | 0.15664 | 0.15664 | 0.15664 | 0.15664 | 0.15664 | 0.15664
Reactance of Metallic Sheath Equation
20 | Positive Sequence Impedance |  | [Ω/mile] | 0.022802 + j0.264578 | 0.022812 + j0.264578 | 0.022765 + j0.264578 | 0.022811 + j0.264578 | 0.022802 + j0.264578 | 0.022764 + j0.264578
Positive Sequence Impedance Equation
21 | Negative Sequence Impedance |  | [Ω/mile] | 0.022802 + j0.264578 | 0.022812 + j0.264578 | 0.022765 + j0.264578 | 0.022811 + j0.264578 | 0.022802 + j0.264578 | 0.022764 + j0.264578
Negative Sequence Impedance Equation
22 | Zero Sequence Impedance |  | [Ω/mile] | 0.603435 + j0.107934 | 0.603429 + j0.107934 | 0.603462 + j0.107934 | 0.603429 + j0.107934 | 0.603436 + j0.107934 | 0.603462 + j0.107934
Zero Sequence Impedance Equation
23 | Surge Impedance |  | [Ω] | 40.3405 | 40.3405 | 40.3405 | 40.3405 | 40.3405 | 40.3405
Surge Impedance Equation
Others
24 | Dielectric Stress at Insulation Inner Surface |  | [kV/in] | 192.0593 | 192.0593 | 192.0593 | 192.0593 | 192.0593 | 192.0593
Dielectric Stress at Insulation Inner Surface Equation
25 | Dielectric Stress at Insulation Outer Surface |  | [kV/in] | 114.3782 | 114.3782 | 114.3782 | 114.3782 | 114.3782 | 114.3782
26 | Insulation Resistance at 60°F (15.8°C) |  | [㏁.1000ft] | 418.235 | 418.235 | 418.235 | 418.235 | 418.235 | 418.235
Insulation Resistance at 60°F (15.8°C) Equation
27 | Reduction Factor (2pt bonded & single metallic screen) |  |  | n/a | n/a | n/a | n/a | n/a | n/a
Reduction Factor Equation (2pt bonded & single metallic screen)
28 | Charging Current for One Cable (Phase) |  | [A/mile] | 21.5893 | 21.5893 | 21.5893 | 21.5893 | 21.5893 | 21.5893
Charging Current Equation for One Cable (Phase)
29 | Charging Capacity of three phase system at Uo |  | [kvar/mile] | 8600.5667 | 8600.5667 | 8600.5667 | 8600.5667 | 8600.5667 | 8600.5667
Charging Capacity of three phase system at Uo Equation
30 | Voltage drop for Three Phase System |  | [V/A/mile] | 0.039495 | 0.039511 | 0.039429 | 0.03951 | 0.039494 | 0.039429
Voltage drop Equation for Three Phase System
31 | Induced Voltage (standing) on Sheath |  | [V/mile] | 182.3237 | 177.388 | 179.9347 | 177.388 | 182.3237 | 179.9347
32 | Induced Voltage angle on Sheath |  | [°] | -30.4145 | 89.5046 | -149.0926 | -29.5046 | 90.4145 | -150.9074
33 | Induced Voltage (standing) on Concentric Wires |  | [V/mile] | 180.6786 | 175.7429 | 178.2898 | 175.7429 | 180.6786 | 178.2898
34 | Induced Voltage angle on Concentric Wires |  | [°] | -30.4183 | 89.5 | -149.0842 | -29.5 | 90.4183 | -150.9158
35 | Induced current on Metallic Screen |  | [A] | 0 | 0 | 0 | 0 | 0 | 0
Induced current on Metallic Screen Equation

## Steady State
Cable Parameters under Normal Operation
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | CAYUGA 230 KV HDD soil 90
Date: |  | 1/8/2026 1:59:22 PM
No. | Symbol | Description | Unit | Cable No.1 | Cable No.2 | Cable No.3 | Cable No.4 | Cable No.5 | Cable No.6
1 |  | Cable Equipment ID |  | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL
Normal Operation IEC 60287-1-1
Conductor AC Resistance
2 | R₀ | DC Resistance of the conductor at 20°C | [Ω/mile] | 0.011162 | 0.011162 | 0.011162 | 0.011162 | 0.011162 | 0.011162
DC Resistance of the conductor at 20°C Equation
3 | R' | DC Resistance of Conductor at Operating Temperature | [Ω/mile] | 0.014158 | 0.01417 | 0.014113 | 0.014169 | 0.014158 | 0.014112
DC Resistance of Conductor at Operating Temperature Equation
4 | dc | Conductor Diameter | [in] | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48
5 | s | Distance Between Conductor Axes | [in] | 8.5467 | 8.5467 | 8.5467 | 8.5467 | 8.5467 | 8.5467
6 | ks | Factor Used for xs Calculation (Skin Effect) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
7 | kp | Factor Used for xp Calculation (Proximity Effect) |  | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37
8 | Xs² | Component of Ys Calculation (Skin Effect) |  | 13.7127 | 13.7015 | 13.7569 | 13.7022 | 13.7132 | 13.7572
Component of Ys Calculation (Skin Effect) Equation
9 | Xp² | Component of Yp Calculation (Proximity Effect) |  | 6.3421 | 6.3369 | 6.3626 | 6.3373 | 6.3424 | 6.3627
Component of Yp Calculation (Proximity Effect) Equation
10 | ys | Skin Effect Factor |  | 0.57048 | 0.56988 | 0.57286 | 0.56991 | 0.57051 | 0.57288
Skin Effect Factor Equation
11 | yp | Proximity Effect Factor |  | 0.040062 | 0.040028 | 0.040196 | 0.04003 | 0.040063 | 0.040196
Proximity Effect Factor Equation
12 | R | AC Resistance of Conductor at Operating Temperature | [Ω/mile] | 0.022802 | 0.022812 | 0.022765 | 0.022811 | 0.022802 | 0.022764
AC Resistance of Conductor at Operating Temperature Equation
Dielectric Losses
13 | tanδ | Dielectric Loss Factor |  | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001
14 | ε | Insulation Relative Permittivity |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
15 | C | Cable Capacitance | [µF/mile] | 0.4313 | 0.4313 | 0.4313 | 0.4313 | 0.4313 | 0.4313
Cable Capacitance Equation
16 | U₀ | Voltage | [kV] | 132.7906 | 132.7906 | 132.7906 | 132.7906 | 132.7906 | 132.7906
17 | Wd | Cable Dielectric Losses Per Phase | [W/ft] | 0.54297 | 0.54297 | 0.54297 | 0.54297 | 0.54297 | 0.54297
Cable Dielectric Losses Per Phase Equation
Circulating Loss Factor
18 | ƛ'sa | Circulating Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
Circulating Loss Factor Equation
19 | ƛ'₁ | Screen Loss Factor Caused by Circulating Current |  | 0 | 0 | 0 | 0 | 0 | 0
Screen Loss Factor Equation
Eddy Loss Factor
20 | Rs | AC Resistance used for Eddy Loss Factor computation | [Ω/mile] | 0.72799 | 0.72859 | 0.72562 | 0.72855 | 0.72796 | 0.72561
21 | d | Mean diameter used for Eddy Loss Factor computation | [in] | 4.673 | 4.673 | 4.673 | 4.673 | 4.673 | 4.673
22 | ρs | Electrical Resistivity used for Eddy Loss Factor computation | [Ω.ft] | 7.0282e-08 | 7.0341e-08 | 7.0052e-08 | 7.0338e-08 | 7.0279e-08 | 7.0052e-08
23 | Ds | External diameter used for Eddy Loss Factor computation | [in] | 4.678 | 4.678 | 4.678 | 4.678 | 4.678 | 4.678
24 | ts | Thickness used for Eddy Loss Factor computation | [in] | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005
25 | β₁ | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 148.7102 | 148.6489 | 148.9524 | 148.6526 | 148.713 | 148.9542
β₁ Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 Equation
26 | gs | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 1.0001 | 1.0001 | 1.0001 | 1.0001 | 1.0001 | 1.0001
gs Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 Equation
27 | m | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 0.08334 | 0.083272 | 0.083612 | 0.083276 | 0.083343 | 0.083614
m Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 Equation
28 | ƛ₀ | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 0.0015465 | 0.001544 | 0.0015566 | 0.0015441 | 0.0015466 | 0.0015566
ƛ₁ Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 Equation
29 | Δ₁ | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 0.034975 | 0.034977 | 0.034966 | 0.034977 | 0.034975 | 0.034965
Δ₁ Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 Equation
30 | Δ₂ | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 0 | 0 | 0 | 0 | 0 | 0
Δ₂ Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 Equation
31 | F | Milliken conductor Effect |  | 1 | 1 | 1 | 1 | 1 | 1
Milliken conductor Effect Equation
32 | Fpipe | Magnetic effect factor due to pipe |  | 1 | 1 | 1 | 1 | 1 | 1
Magnetic effect factor due to pipe Equation
33 | Farmour | Magnetic effect factor due to armour |  | 1 | 1 | 1 | 1 | 1 | 1
Magnetic effect factor due to armour Equation
34 | ƛ''₁ | Screen Loss Factor Caused by Eddy Current |  | 0.051107 | 0.051044 | 0.051356 | 0.051048 | 0.05111 | 0.051358
Screen Loss Factor Caused by Eddy Current Equation
Metallic Screen Loss factor
35 | ƛ₁ | Screen Loss Factor |  | 0.051107 | 0.051044 | 0.051356 | 0.051048 | 0.05111 | 0.051358
Screen Loss Factor Equation
Armour and Pipe Loss Factor
36 | ƛ₂a | Armour Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
Armour Loss Factor Equation
37 | ƛ₂pipe | Pipe Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
Pipe Loss Factor Equation
38 | ƛ₂ | Armour Loss Factor + Pipe Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
Armour Loss Factor + Pipe Loss Factor Equation
Normal Operation IEC 60287-2-1
39 | T₁ | Thermal Resistance Between Conductor and Screen | [K.m/W] | 0.34068 | 0.34068 | 0.34068 | 0.34068 | 0.34068 | 0.34068
Thermal Resistance Between Conductor and Screen Equation
40 | t₁ | Insulation Thickness Between Conductor and Screen | [in] | 1.094 | 1.094 | 1.094 | 1.094 | 1.094 | 1.094
41 | ρTi | Thermal Resistivity of Insulation | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
42 | T₃ | Thermal Resistance of Jacket/Pipe Coating | [K.m/W] | 0.074098 | 0.074098 | 0.074098 | 0.074098 | 0.074098 | 0.074098
Thermal Resistance of Jacket/Pipe Coating Equation
43 | t₃ | Thickness of Jacket/Pipe Coating | [in] | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34
44 | ρTJ | Thermal Resistivity of Jacket/Pipe Coating | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
45 | T Conductor Shield | Thermal resistance | [K.m/W] | 0.029074 | 0.029074 | 0.029074 | 0.029074 | 0.029074 | 0.029074
46 |  | Thermal resistance equation
47 |  | Thermal resistivity | [K.m/W] | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
48 |  | Layer thickness | [in] | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094
49 |  | Internal diameter | [in] | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48
50 | T Insulation | Thermal resistance | [K.m/W] | 0.28871 | 0.28871 | 0.28871 | 0.28871 | 0.28871 | 0.28871
51 |  | Thermal resistance equation
52 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
53 |  | Layer thickness | [in] | 0.906 | 0.906 | 0.906 | 0.906 | 0.906 | 0.906
54 |  | Internal diameter | [in] | 2.668 | 2.668 | 2.668 | 2.668 | 2.668 | 2.668
55 | T Insulation Screen | Thermal resistance | [K.m/W] | 0.022899 | 0.022899 | 0.022899 | 0.022899 | 0.022899 | 0.022899
56 |  | Thermal resistance equation
57 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
58 |  | Layer thickness | [in] | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094
59 |  | Internal diameter | [in] | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48
60 | T Sheath | Thermal resistance | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
61 |  | Thermal resistance equation
62 |  | Thermal resistivity | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
63 |  | Layer thickness | [in] | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005
64 |  | Internal diameter | [in] | 4.668 | 4.668 | 4.668 | 4.668 | 4.668 | 4.668
65 | T Concentric wires | Thermal resistance | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
66 |  | Thermal resistance equation
67 |  | Thermal resistivity | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
68 |  | Layer thickness | [in] | 0.05076 | 0.05076 | 0.05076 | 0.05076 | 0.05076 | 0.05076
69 |  | Internal diameter | [in] | 4.678 | 4.678 | 4.678 | 4.678 | 4.678 | 4.678
70 | T Jacket | Thermal resistance | [K.m/W] | 0.074098 | 0.074098 | 0.074098 | 0.074098 | 0.074098 | 0.074098
71 |  | Thermal resistance equation
72 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
73 |  | Layer thickness | [in] | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34
74 |  | Internal diameter | [in] | 4.7795 | 4.7795 | 4.7795 | 4.7795 | 4.7795 | 4.7795
Thermal resistance inside the duct
75 | U | Constant from IEC6028721 clause4272 |  | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87
76 | V | Constant from IEC6028721 clause4272 |  | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312
77 | Y | Constant from IEC6028721 clause4272 |  | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037
78 | θm | Mean temperature of the medium in conduit | [°C] | 78.003 | 78.2654 | 76.9682 | 78.2496 | 77.991 | 76.9607
79 | Deq | Equivalent diameter of the cables inside the conduit | [in] | 5.4595 | 5.4595 | 5.4595 | 5.4595 | 5.4595 | 5.4595
80 | T₄' | Thermal resistance of the medium in conduit | [K.m/W] | 0.20045 | 0.20017 | 0.2016 | 0.20018 | 0.20047 | 0.20161
Thermal resistance of the medium in conduit Equation
Thermal resistance of the duct
81 | Do | Outer diameter of the conduit | [in] | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47
82 | Di | Inner diameter of the conduit | [in] | 6.963 | 6.963 | 6.963 | 6.963 | 6.963 | 6.963
83 | ρT | Thermal resistivity of the conduit material | [K.m/W] | 6 | 6 | 6 | 6 | 6 | 6
84 | T₄'' | Thermal resistance of the conduit | [K.m/W] | 0.18709 | 0.18709 | 0.18709 | 0.18709 | 0.18709 | 0.18709
Thermal resistance of the conduit Equation
Thermal resistance of the external medium
85 | L | Depth of cable/conduit axis | [ft] | 29.7485 | 29.7485 | 29.1315 | 29.7485 | 29.7485 | 29.1315
86 | De / Do | External diameter of the cable conduit | [ft] | 0.70583 | 0.70583 | 0.70583 | 0.70583 | 0.70583 | 0.70583
87 | u | Geometric factor as per IEC60287-2-1 clause 4.2.2 |  | 84.2932 | 84.2932 | 82.5449 | 84.2932 | 84.2932 | 82.5449
Geometric factor Equation as per IEC60287-2-1 clause 4.2.2
88 | ρTs | Thermal resistivity of the soil | [K.m/W] | 1.0549 | 1.055 | 1.1588 | 1.0541 | 1.0543 | 1.1585
89 | T₄'''self | Thermal resistance of the cable isolated | [K.m/W] | 0.86082 | 0.86097 | 0.94181 | 0.86021 | 0.86038 | 0.94156
Thermal resistance of the cable isolated Equation
90 | T₄'''mutual | Thermal resistance associated to the temperature rise due to surrounding heat sources | [K.m/W] | 1.856 | 1.8674 | 1.7296 | 1.8675 | 1.856 | 1.7295
Thermal resistance associated to the temperature rise due to surrounding heat sources Equation
91 | Δθint | Temperature rise due to surrounding heat sources | [°C] | 39.419 | 39.6736 | 36.6851 | 39.6743 | 39.4166 | 36.6831
Temperature rise due to surrounding heat sources Equation
92 | T₄''' | Thermal resistance of the external medium | [K.m/W] | 2.7169 | 2.7284 | 2.6714 | 2.7277 | 2.7163 | 2.6711
Thermal resistance of the external medium Equation
Thermal Capacitance IEC 853-2
93 | Q Conductor | Thermal capacitance | [J/m.K] | 8747.9442 | 8747.9442 | 8747.9442 | 8747.9442 | 8747.9442 | 8747.9442
94 |  | Thermal capacitance equation
95 |  | Material surface | [in²] | 3.9302 | 3.9302 | 3.9302 | 3.9302 | 3.9302 | 3.9302
96 |  | Volumetric specific heat of the material | [J/(K*m³)] | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000
97 | Q Conductor Shield | Thermal capacitance | [J/m.K] | 1176.969 | 1176.969 | 1176.969 | 1176.969 | 1176.969 | 1176.969
98 |  | Thermal capacitance equation
99 |  | External diameter | [in] | 2.668 | 2.668 | 2.668 | 2.668 | 2.668 | 2.668
100 |  | Internal diameter | [in] | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48
101 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
102 | Q1 Insulation | Thermal capacitance | [J/m.K] | 5879.1234 | 5879.1234 | 5879.1234 | 5879.1234 | 5879.1234 | 5879.1234
103 |  | Thermal capacitance equation
104 |  | External diameter | [in] | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48
105 |  | Internal diameter | [in] | 2.668 | 2.668 | 2.668 | 2.668 | 2.668 | 2.668
106 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
107 | Q2 Insulation | Thermal capacitance | [J/m.K] | 9871.9913 | 9871.9913 | 9871.9913 | 9871.9913 | 9871.9913 | 9871.9913
108 |  | Thermal capacitance equation
109 |  | External diameter | [in] | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48
110 |  | Internal diameter | [in] | 2.668 | 2.668 | 2.668 | 2.668 | 2.668 | 2.668
111 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
112 | Q Insulation Screen | Thermal capacitance | [J/m.K] | 2091.4738 | 2091.4738 | 2091.4738 | 2091.4738 | 2091.4738 | 2091.4738
113 |  | Thermal capacitance equation
114 |  | External diameter | [in] | 4.668 | 4.668 | 4.668 | 4.668 | 4.668 | 4.668
115 |  | Internal diameter | [in] | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48
116 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
117 | Q Sheath | Thermal capacitance | [J/m.K] | 163.3798 | 163.3798 | 163.3798 | 163.3798 | 163.3798 | 163.3798
118 |  | Thermal capacitance equation
119 |  | External diameter | [in] | 4.678 | 4.678 | 4.678 | 4.678 | 4.678 | 4.678
120 |  | Internal diameter | [in] | 4.668 | 4.668 | 4.668 | 4.668 | 4.668 | 4.668
121 |  | Volumetric specific heat of the material | [J/(K*m³)] | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000
122 | Q Concentric wires | Thermal capacitance | [J/m.K] | 6.2441 | 6.2441 | 6.2441 | 6.2441 | 6.2441 | 6.2441
123 |  | Thermal capacitance equation
124 |  | Number of armour wires |  | 40 | 40 | 40 | 40 | 40 | 40
125 |  | Mean diameter of armour wire | [in] | 0.05076 | 0.05076 | 0.05076 | 0.05076 | 0.05076 | 0.05076
126 |  | Length of lay | [in] | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937
127 |  | Mean diameter of armour | [in] | 4.7288 | 4.7288 | 4.7288 | 4.7288 | 4.7288 | 4.7288
128 |  | Wire Shape is half-circle |  | 0 | 0 | 0 | 0 | 0 | 0
129 | Q Jacket | Thermal capacitance | [J/m.K] | 8467.1389 | 8467.1389 | 8467.1389 | 8467.1389 | 8467.1389 | 8467.1389
130 |  | Thermal capacitance equation
131 |  | External diameter | [in] | 5.4595 | 5.4595 | 5.4595 | 5.4595 | 5.4595 | 5.4595
132 |  | Internal diameter | [in] | 4.7795 | 4.7795 | 4.7795 | 4.7795 | 4.7795 | 4.7795
133 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
Ampacity
134 | T₄ | Total external thermal resistance | [K.m/W] | 3.1044 | 3.1156 | 3.0601 | 3.115 | 3.1039 | 3.0598
Total external thermal resistance Equation
135 | I | Cable core ampacity | [A] | 1143 | 1143 | 1143 | 1143 | 1143 | 1143
Cable core ampacity Equation

## Short Circuit
Cable Short Circuit
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | CAYUGA 230 KV HDD soil 90
Date: |  | 1/8/2026 1:59:22 PM
Symbol | Description |  | Unit | Circuit No. 1
| Cable Equipment ID |  |  | CAYUGA 230KV 5000 KCMIL
|  |  |  | Conductor |  |  | Sheath |  |  | Concentric neutral/Skid wires
|  |  |  | A | B | C | A | B | C | A | B | C
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2535.636 | 2535.636 | 2535.636 | 47.3569 | 47.3569 | 47.3569 | 52.2225 | 52.2225 | 52.2225
θi | Initial Temperature |  | [°C] | 88.3127 | 88.5754 | 87.2769 | 81.7032 | 81.9632 | 80.6779 | 81.7032 | 81.9632 | 80.6779
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 250 | 250 | 150 | 150 | 150 | 150 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1153007.4204 | 1151852.1935 | 1157561.7522 | 14944.5561 | 14913.1235 | 15068.1449 | 16480.022 | 16445.3599 | 16616.3089
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1154783.2643 | 1153626.2581 | 1159344.6106 | 18582.5984 | 18543.514 | 18736.2732 | 16892.3666 | 16856.8372 | 17032.0634
Symbol | Description |  | Unit | Circuit No. 2
| Cable Equipment ID |  |  | CAYUGA 230KV 5000 KCMIL
|  |  |  | Conductor |  |  | Sheath |  |  | Concentric neutral/Skid wires
|  |  |  | A | B | C | A | B | C | A | B | C
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2535.636 | 2535.636 | 2535.636 | 47.3569 | 47.3569 | 47.3569 | 52.2225 | 52.2225 | 52.2225
θi | Initial Temperature |  | [°C] | 88.5595 | 88.3006 | 87.2693 | 81.9475 | 81.6912 | 80.6704 | 81.9475 | 81.6912 | 80.6704
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 250 | 250 | 150 | 150 | 150 | 150 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1151921.9344 | 1153060.6668 | 1157595.218 | 14915.0222 | 14946.0042 | 15069.0513 | 16447.4537 | 16481.6189 | 16617.3083
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1153696.1065 | 1154836.5927 | 1159378.1279 | 18545.8749 | 18584.399 | 18737.4002 | 16858.9833 | 16894.0034 | 17033.0879