## General Su...- CAYUGA 230 KV-53
General Summary Report
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | CAYUGA air filled Oct 30 2025
Date: |  | 1/8/2026 1:58:20 PM
Simulation Data
Installation type: |  | Trough
Steady State Option |  | Temperature
Ambient temperature [°C] |  | 36
Consider Electrical interaction between circuits |  | No
Induced current in metallic layers as a fraction of conductor current (applied to all single phase circuits) [A] |  | 0
Installation Type:Unfilled Trough
Method used |  | IEC
Ambient Air Temperature [°C] |  | 36
Trough Installation Exposition to Sun |  | Exposed
Cover Thickness [ft] |  | 0.625
Trough Width [ft] |  | 7
Trough Height [ft] |  | 3
General Cable Information
Cable ID |  | Number of Cores | Conductor Construction | Voltage [kV] | Conductor Area [mm²] | Cable Overall Diameter [in] | Maximum Steady-State Conductor Temperature [ºC] | Maximum Emergency Conductor Temperature [ºC]
CAYUGA 230KV 5000 KCMIL |  | Single Core | 6 Segments | 230 | 2535.636 | 5.4595 | 90 | 110
Detailed Cable Information
Cable ID |  | Conductor | Insulation | Sheath / Tape | Concentric Wires | Filler | Armour | Jacket / Armour Serving
CAYUGA 230KV 5000 KCMIL |  | Copper | XLPE Unfilled | Copper | Copper | n/a | n/a | Polyethylene
General Input Data
Cable | Cable ID | Circuit No. | Phase | Fq [Hz] | X [ft] | Y [ft] | DLF [p.u.] | Sheath / Shield Bonding
Cable Index Number | Cable Equipment ID | Circuit No. | Cable Phase | Operating Frequency | X coordinate | Y coordinate | Daily Load Factor | Bonding Type
1 | CAYUGA 230KV 5000 KCMIL | 1 | A | 60 | -0.72748 | 3.3813 | 1 | 1 Conductor 1 Point Bonded Triangular
2 | CAYUGA 230KV 5000 KCMIL | 1 | B | 60 | -0.27252 | 3.3813 | 1 | 1 Conductor 1 Point Bonded Triangular
3 | CAYUGA 230KV 5000 KCMIL | 1 | C | 60 | -0.5 | 2.9873 | 1 | 1 Conductor 1 Point Bonded Triangular
4 | CAYUGA 230KV 5000 KCMIL | 2 | A | 60 | 0.27252 | 3.3813 | 1 | 1 Conductor 1 Point Bonded Triangular
5 | CAYUGA 230KV 5000 KCMIL | 2 | B | 60 | 0.72748 | 3.3813 | 1 | 1 Conductor 1 Point Bonded Triangular
6 | CAYUGA 230KV 5000 KCMIL | 2 | C | 60 | 0.5 | 2.9873 | 1 | 1 Conductor 1 Point Bonded Triangular
Ampacity and Temperatures
Cable | Cable ID | I [A] | θc [°C] | θs [°C] | θa [°C] | θsurf [°C] | θduct [°C] | θair / θcasing [°C]
Cable Index Number | Cable Equipment ID | Steady State Ampacity | Conductor temperature | Sheath/Shield temperature | Armour temperature | Cable surface temperature | Duct surface temperature | Mean air temperature in the tunnel / Casing surface temperature
1 | CAYUGA 230KV 5000 KCMIL | 1288 | 72.7774 | 65.1948 | n/a | 63.2755 | n/a | n/a
2 | CAYUGA 230KV 5000 KCMIL | 1288 | 72.7774 | 65.1948 | n/a | 63.2755 | n/a | n/a
3 | CAYUGA 230KV 5000 KCMIL | 1288 | 72.7774 | 65.1948 | n/a | 63.2755 | n/a | n/a
4 | CAYUGA 230KV 5000 KCMIL | 1288 | 72.7774 | 65.1948 | n/a | 63.2755 | n/a | n/a
5 | CAYUGA 230KV 5000 KCMIL | 1288 | 72.7774 | 65.1948 | n/a | 63.2755 | n/a | n/a
6 | CAYUGA 230KV 5000 KCMIL | 1288 | 72.7774 | 65.1948 | n/a | 63.2755 | n/a | n/a
Electrical Resistances
Cable | Cable ID | R₀ [Ω/mile] | ys | yp | R [Ω/mile] | R's [Ω/mile] | R'w [Ω/mile] | R'a [Ω/mile]
Cable Index Number | Cable Equipment ID | DC Resistance of the conductor at 20°C | Skin Effect Factor | Proximity Effect Factor | AC Resistance of Conductor at Operating Temperature | DC Resistance of Sheath at Operating Temperature | DC Resistance of Concentric Wires at Operating Temperature | DC Resistance of Armor at Operating Temperature
1 | CAYUGA 230KV 5000 KCMIL | 0.011162 | 0.43344 | 0.10474 | 0.020729 | 0.68997 | 23.6178 | n/a
2 | CAYUGA 230KV 5000 KCMIL | 0.011162 | 0.43344 | 0.10474 | 0.020729 | 0.68997 | 23.6178 | n/a
3 | CAYUGA 230KV 5000 KCMIL | 0.011162 | 0.43344 | 0.10474 | 0.020729 | 0.68997 | 23.6178 | n/a
4 | CAYUGA 230KV 5000 KCMIL | 0.011162 | 0.43344 | 0.10474 | 0.020729 | 0.68997 | 23.6178 | n/a
5 | CAYUGA 230KV 5000 KCMIL | 0.011162 | 0.43344 | 0.10474 | 0.020729 | 0.68997 | 23.6178 | n/a
6 | CAYUGA 230KV 5000 KCMIL | 0.011162 | 0.43344 | 0.10474 | 0.020729 | 0.68997 | 23.6178 | n/a
Thermal Resistances
Cable | Cable ID | T₁ [K.m/W] | T₂ [K.m/W] | T₃ [K.m/W] | T₄' [K.m/W] | T₄'' [K.m/W] | T₄''' [K.m/W] | T₄ [K.m/W]
Cable Index Number | Cable Equipment ID | Thermal resistance of insulation | Thermal resistance of bedding | Thermal resistance of outer covering | Thermal resistance inside the duct | Thermal resistance of the duct | Thermal resistance of the external medium | Total external thermal resistance
1 | CAYUGA 230KV 5000 KCMIL | 0.34068 | 0 | 0.074098 | n/a | n/a | 0.53198 | 0.53198
2 | CAYUGA 230KV 5000 KCMIL | 0.34068 | 0 | 0.074098 | n/a | n/a | 0.53198 | 0.53198
3 | CAYUGA 230KV 5000 KCMIL | 0.34068 | 0 | 0.074098 | n/a | n/a | 0.53198 | 0.53198
4 | CAYUGA 230KV 5000 KCMIL | 0.34068 | 0 | 0.074098 | n/a | n/a | 0.53198 | 0.53198
5 | CAYUGA 230KV 5000 KCMIL | 0.34068 | 0 | 0.074098 | n/a | n/a | 0.53198 | 0.53198
6 | CAYUGA 230KV 5000 KCMIL | 0.34068 | 0 | 0.074098 | n/a | n/a | 0.53198 | 0.53198
Losses
Cable | Cable ID | Wc [W/ft] | Wd [W/ft] | Ws [W/ft] | Wa [W/ft] | Wt [W/ft] | ƛ₁ | ƛ₂
Cable Index Number | Cable Equipment ID | Conductor Losses | Dielectric Losses | Metallic Screen Losses | Armor/Pipe Losses | Total Losses | Screen Loss Factor | Armour Loss Factor + Pipe Loss Factor
1 | CAYUGA 230KV 5000 KCMIL | 6.513 | 0.54297 | 0.98351 | 0 | 8.0395 | 0.15101 | 0
2 | CAYUGA 230KV 5000 KCMIL | 6.513 | 0.54297 | 0.98351 | 0 | 8.0395 | 0.15101 | 0
3 | CAYUGA 230KV 5000 KCMIL | 6.513 | 0.54297 | 0.98351 | 0 | 8.0395 | 0.15101 | 0
4 | CAYUGA 230KV 5000 KCMIL | 6.513 | 0.54297 | 0.98351 | 0 | 8.0395 | 0.15101 | 0
5 | CAYUGA 230KV 5000 KCMIL | 6.513 | 0.54297 | 0.98351 | 0 | 8.0395 | 0.15101 | 0
6 | CAYUGA 230KV 5000 KCMIL | 6.513 | 0.54297 | 0.98351 | 0 | 8.0395 | 0.15101 | 0
Complementary Information
Cable | Cable ID | Δθint [°C] | [A] | [µF/mile] | [Ω] | [Ω/mile] | [Ω/mile] | [V/A/mile]
Cable Index Number | Cable Equipment ID | Temperature rise due to surrounding heat sources | Induced current on Metallic Screen | Cable Capacitance | Surge Impedance | Reactance of Conductor | Reactance of Metallic Sheath | Voltage drop for Three Phase System
1 | CAYUGA 230KV 5000 KCMIL | 0 | 0 | 0.4313 | 35.9563 | 0.21019 | 0.10226 | 0.035904
2 | CAYUGA 230KV 5000 KCMIL | 0 | 0 | 0.4313 | 35.9563 | 0.21019 | 0.10226 | 0.035904
3 | CAYUGA 230KV 5000 KCMIL | 0 | 0 | 0.4313 | 35.9563 | 0.21019 | 0.10226 | 0.035904
4 | CAYUGA 230KV 5000 KCMIL | 0 | 0 | 0.4313 | 35.9563 | 0.21019 | 0.10226 | 0.035904
5 | CAYUGA 230KV 5000 KCMIL | 0 | 0 | 0.4313 | 35.9563 | 0.21019 | 0.10226 | 0.035904
6 | CAYUGA 230KV 5000 KCMIL | 0 | 0 | 0.4313 | 35.9563 | 0.21019 | 0.10226 | 0.035904

## Study Summary
Study Summary
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | CAYUGA air filled Oct 30 2025
Date: |  | 1/8/2026 1:58:20 PM
General Simulation Data
Steady State Option | [8 empty] | Temperature
Consider Electrical interaction between circuits | [8 empty] | No
Induced currents in metallic layers as a fraction of conductor current (applied to all single phase circuits) : | [8 empty] | 0
Conductor Resistances Computation Option: | [8 empty] | IEC-228
Standard Settings Options
General guidance | [8 empty] | Custom
Factor on RAC due to magnetic armour | [8 empty] | CIGREGuidance
Factor on RAC due to magnetic duct | [8 empty] | CIGREGuidance
Factor on ƛ₁ due to magnetic armour | [8 empty] | CYMCAPGuidance
Factor on ƛ₁ due to magnetic duct | [8 empty] | CIGREGuidance
Factor on ƛ₂ due to ƛ'₁ | [8 empty] | CYMCAPGuidance
ƛ''₁ computation | [8 empty] | CIGREGuidance
ƛ₂pipe computation | [8 empty] | CYMCAPGuidance
Wd computation | [8 empty] | CIGREGuidance
T₂ computation | [8 empty] | CIGREGuidance
T₄ computation | [8 empty] | CYMCAPGuidance
Installation Type:Unfilled Trough
Method used | [8 empty] | IEC
Ambient Air Temperature [°C] | [8 empty] | 36
Trough Installation Exposition to Sun | [8 empty] | Exposed
Cover Thickness [ft] | [8 empty] | 0.625
Trough Width [ft] | [8 empty] | 7
Trough Height [ft] | [8 empty] | 3
Results Summary
Cable No. | Cable ID | Circuit No. | Feeder ID | Cable Phase | Cable Frequency | Daily Load Factor | X coordinate [ft] | Y coordinate [ft] | Conductor temperature [°C] | Ampacity [A]
1 | CAYUGA 230KV 5000 KCMIL | 1 |  | A | 60 | 1 | -0.72748 | 3.3813 | 72.7774 | 1288
2 | CAYUGA 230KV 5000 KCMIL | 1 |  | B | 60 | 1 | -0.27252 | 3.3813 | 72.7774 | 1288
3 | CAYUGA 230KV 5000 KCMIL | 1 |  | C | 60 | 1 | -0.5 | 2.9873 | 72.7774 | 1288
4 | CAYUGA 230KV 5000 KCMIL | 2 |  | A | 60 | 1 | 0.27252 | 3.3813 | 72.7774 | 1288
5 | CAYUGA 230KV 5000 KCMIL | 2 |  | B | 60 | 1 | 0.72748 | 3.3813 | 72.7774 | 1288
6 | CAYUGA 230KV 5000 KCMIL | 2 |  | C | 60 | 1 | 0.5 | 2.9873 | 72.7774 | 1288

## Steady State Summary
Steady State Summary
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | CAYUGA air filled Oct 30 2025
Date: |  | 1/8/2026 1:58:20 PM
Simulation Data
Installation type: |  | Trough
Steady State Option |  | Temperature
Ambient temperature [°C] |  | 36
Consider Electrical interaction between circuits |  | No
Induced current in metallic layers as a fraction of conductor current (applied to all single phase circuits) [A] |  | 0
Variable | Description |  | Unit | Cables
Cable No. | Cable Index Number |  |  | 1 | 2 | 3 | 4 | 5 | 6
General Input Data
Cable ID | Cable Equipment ID |  |  | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL
Circuit No. | Circuit No. |  |  | 1 | 1 | 1 | 2 | 2 | 2
Phase | Cable Phase |  |  | A | B | C | A | B | C
Fq | Operating Frequency |  | [Hz] | 60 | 60 | 60 | 60 | 60 | 60
x | X coordinate |  | [ft] | -0.72748 | -0.27252 | -0.5 | 0.27252 | 0.72748 | 0.5
y | Y coordinate |  | [ft] | 3.3813 | 3.3813 | 2.9873 | 3.3813 | 3.3813 | 2.9873
DLF | Daily Load Factor |  | [p.u.] | bar: Cables 1 to Cables 6
| Bonding Type |  |  | 1 Conductor 1 Point Bonded Triangular | 1 Conductor 1 Point Bonded Triangular | 1 Conductor 1 Point Bonded Triangular | 1 Conductor 1 Point Bonded Triangular | 1 Conductor 1 Point Bonded Triangular | 1 Conductor 1 Point Bonded Triangular
Ampacity
I | Steady State Ampacity |  | [A] | 1288 | 1288 | 1288 | 1288 | 1288 | 1288
I₀ | Steady State Ampacity without insulation temperature drop constraint |  | [A] | n/a | n/a | n/a | n/a | n/a | n/a
Temperatures
θc | Conductor temperature |  | [°C] | 72.7774 | 72.7774 | 72.7774 | 72.7774 | 72.7774 | 72.7774
Δθins | Temperature drop across the insulation |  | [°C] | n/a | n/a | n/a | n/a | n/a | n/a
θs | Sheath/Shield temperature |  | [°C] | 65.1948 | 65.1948 | 65.1948 | 65.1948 | 65.1948 | 65.1948
θa | Armour temperature |  | [°C] | n/a | n/a | n/a | n/a | n/a | n/a
θsurf | Cable surface temperature |  | [°C] | 63.2755 | 63.2755 | 63.2755 | 63.2755 | 63.2755 | 63.2755
θduct | Duct surface temperature |  | [°C] | n/a | n/a | n/a | n/a | n/a | n/a
Resistances
R₀ | DC Resistance of the conductor at 20°C |  | [Ω/mile] | 0.011162 | 0.011162 | 0.011162 | 0.011162 | 0.011162 | 0.011162
R | AC Resistance of the Conductor at Operating Temperature |  | [Ω/mile] | 0.020729 | 0.020729 | 0.020729 | 0.020729 | 0.020729 | 0.020729
ys | Skin Effect Factor |  |  | 0.43344 | 0.43344 | 0.43344 | 0.43344 | 0.43344 | 0.43344
yp | Proximity Effect Factor |  |  | 0.10474 | 0.10474 | 0.10474 | 0.10474 | 0.10474 | 0.10474
Losses
Wc | Conductor Losses |  | [W/ft] | 6.513 | 6.513 | 6.513 | 6.513 | 6.513 | 6.513
Wd | Dielectric Losses |  | [W/ft] | 0.54297 | 0.54297 | 0.54297 | 0.54297 | 0.54297 | 0.54297
Ws | Metallic Screen Losses |  | [W/ft] | 0.98351 | 0.98351 | 0.98351 | 0.98351 | 0.98351 | 0.98351
Wa | Armor/Pipe Losses |  | [W/ft] | 0 | 0 | 0 | 0 | 0 | 0
Wt | Total Losses |  | [W/ft] | 8.0395 | 8.0395 | 8.0395 | 8.0395 | 8.0395 | 8.0395
ƛ₁ | Screen Loss Factor |  |  | 0.15101 | 0.15101 | 0.15101 | 0.15101 | 0.15101 | 0.15101
ƛ₂ | Armour Loss Factor + Pipe Loss Factor |  |  | 0 | 0 | 0 | 0 | 0 | 0
Thermal resistances
T1 | Thermal Resistance Between Conductor and Screen |  | [K.m/W] | 0.34068 | 0.34068 | 0.34068 | 0.34068 | 0.34068 | 0.34068
T2 | Thermal Resistance Between Screen and Armour |  | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
T3 | Thermal Resistance of the Jacket/Pipe Coating |  | [K.m/W] | 0.074098 | 0.074098 | 0.074098 | 0.074098 | 0.074098 | 0.074098
T4 | Total external thermal resistance |  | [K.m/W] | 0.53198 | 0.53198 | 0.53198 | 0.53198 | 0.53198 | 0.53198
Others
Δθint | Temperature rise due to surrounding heat sources |  | [°C] | 0 | 0 | 0 | 0 | 0 | 0
| Induced Voltage (standing) on Sheath |  | [V/mile] | 182.5291 | 97.1557 | 151.1998 | 97.1557 | 182.5291 | 151.1998
| Induced Voltage angle on Sheath |  | [°] | -35.147 | 49.6866 | -129.2114 | 10.3134 | 95.147 | -170.7886
| Induced Voltage (standing) on Concentric Wires |  | [V/mile] | 180.6829 | 95.7497 | 149.4681 | 95.7497 | 180.6829 | 149.4681
| Induced Voltage angle on Concentric Wires |  | [°] | -35.1997 | 48.9689 | -128.9592 | 11.0311 | 95.1997 | -171.0408
| Induced current on Metallic Screen |  | [A] | 0 | 0 | 0 | 0 | 0 | 0

## Cable - CA...A 230KV 5000 KCMIL
Cables Report
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | CAYUGA air filled Oct 30 2025
Date: |  | 1/8/2026 1:58:20 PM
No. | Description |  | Unit | 1
General Cable Information
1 | Cable Equipment ID |  |  | CAYUGA 230KV 5000 KCMIL
2 | Number of Cores |  |  | Single Core
3 | Voltage |  | [kV] | 230
4 | Conductor Area |  | [in²] | 3.9302
5 | Cable Overall Diameter |  | [in] | 5.4595
6 | Maximum Steady-State Conductor Temperature |  | [°C] | 90
7 | Maximum Emergency Conductor Temperature |  | [°C] | 110
Conductor
8 | Material |  |  | Copper
9 | Electrical Resistivity at 20°C |  | [µΩ.cm] | 1.7241
10 | Temperature Coefficient at 20°C |  | [1/K] | 0.00393
11 | Reciprocal of Temperature Coefficient of Resistance (BETA) |  | [K] | 234.4529
12 | Volumetric Specific Heat (SH) |  | [J/(K*cm³)] | 3.45
13 | Construction |  |  | 6 Segments
14 | Conductor Insulation System |  |  | Extruded
15 | Milliken Wires Construction |  |  | Bare Unidirectional Wires
16 | Ks (Skin Effect Coefficient) |  |  | 0.62
17 | Kp (Proximity Effect Coefficient) |  |  | 0.37
18 | Diameter |  | [in] | 2.48
Conductor Shield
19 | Thickness |  | [in] | 0.094
20 | Diameter |  | [in] | 2.668
Insulation
21 | Material |  |  | XLPE Unfilled
22 | Thermal Resistivity |  | [K.m/W] | 3.5
23 | Dielectric Loss Factor - ( tan delta ) |  |  | 0.001
24 | Relative Permittivity - ( epsilon ) |  |  | 2.5
25 | Specific Insulation Resistance Constant at 60°F - ( K ) |  | [㏁.1000ft] | 1858.0608
26 | Thickness |  | [in] | 0.906
27 | Diameter |  | [in] | 4.48
Insulation Screen
28 | Material |  |  | Semi Conducting Screen
29 | Thickness |  | [in] | 0.094
30 | Diameter |  | [in] | 4.668
Sheath
31 | Is Sheath Around Each Core? |  |  | n/a
32 | Material |  |  | Copper
33 | Electrical Resistivity at 20°C |  | [µΩ.cm] | 1.7241
34 | Temperature Coefficient at 20°C |  | [1/K] | 0.00393
35 | Reciprocal of Temperature Coefficient of Resistance (BETA) |  | [K] | 234.5
36 | Volumetric Specific Heat (SH) |  | [J/(K*cm³)] | 3.45
37 | Corrugation Type |  |  | Non Corrugated
38 | Thickness |  | [in] | 0.005
39 | Diameter |  | [in] | 4.678
Concentric neutral/Skid wires
40 | Are Concentric Neutral Wires Around Each Core? |  |  | n/a
41 | Material |  |  | Copper
42 | Electrical Resistivity at 20°C |  | [µΩ.cm] | 1.7241
43 | Temperature Coefficient at 20°C |  | [1/K] | 0.00393
44 | Reciprocal of Temperature Coefficient of Resistance (BETA) |  | [K] | 234.5
45 | Volumetric Specific Heat (SH) |  | [J/(K*cm³)] | 3.45
46 | Wire Type |  |  | Round Wires
47 | Length of Lay |  | [in] | 0.3937
48 | Number of Wires |  |  | 40
49 | Wire Gauge |  |  | 16
50 | Thickness |  | [in] | 0.05076
51 | Diameter |  | [in] | 4.7795
Jacket
52 | Material |  |  | Polyethylene
53 | Thermal Resistivity |  | [K.m/W] | 3.5
54 | Thickness |  | [in] | 0.34
55 | Diameter |  | [in] | 5.4595
No. | Description |  | Unit | 1
Specific Installation Data
56 | Cable Equipment ID |  |  | CAYUGA 230KV 5000 KCMIL
57 | Cable Frequency |  | [Hz] | 60
58 | Sheath / Shield Bonding |  |  | 1 Conductor 1 Point Bonded Triangular
59 | Loss Factor Constant (ALOS) |  |  | 0.3
60 | Spacing Between Cables in Section |  |  | n/a
Cable ID : CAYUGA 230KV 5000 KCMIL
Cable Title |  | CAYUGA 230KV 5000 kcmil

## Impedances
Cable Impedances & Admittances
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | CAYUGA air filled Oct 30 2025
Date: |  | 1/8/2026 1:58:20 PM
Earth Resistivity: [Ω.m] |  | 100
Frequency: [Hz] |  | 60
Temperature
|  |  | Circuit 1 | [8 empty] | Circuit 2
|  |  | Conductor |  |  | Sheath |  |  | Concentric neutral/Skid wires |  |  | Conductor |  |  | Sheath |  |  | Concentric neutral/Skid wires
|  | Phase | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C
| Temperature | [°C] | 72.7774 | 72.7774 | 72.7774 | 65.1948 | 65.1948 | 65.1948 | 65.1948 | 65.1948 | 65.1948 | 72.7774 | 72.7774 | 72.7774 | 65.1948 | 65.1948 | 65.1948 | 65.1948 | 65.1948 | 65.1948
R_Primitive [Ω/mile]
|  |  | Circuit No. 1 |  |  | Circuit No. 2 |  |  | Circuit No. 1 |  |  | Circuit No. 2 |  |  | Circuit No. 1 |  |  | Circuit No. 2
|  |  | Conductor | [5 empty] | Sheath | [5 empty] | Concentric neutral/Skid wires
|  | Phase | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C
Circuit No. 1 | Conductor | A | 0.11603 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.11603 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.11603 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 2 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.11603 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11603 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11603 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 1 | Sheath | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.78527 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.78527 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.78527 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 2 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.78527 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.78527 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.78527 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 1 | Concentric neutral Skid wires | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 23.7131 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 23.7131 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 23.7131 | 0.095302 | 0.095302 | 0.095302
Circuit No. 2 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 23.7131 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 23.7131 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 23.7131
X Primitive [Ω/mile]
|  |  | Circuit No. 1 |  |  | Circuit No. 2 |  |  | Circuit No. 1 |  |  | Circuit No. 2 |  |  | Circuit No. 1 |  |  | Circuit No. 2
|  |  | Conductor | [5 empty] | Sheath | [5 empty] | Concentric neutral/Skid wires
|  | Phase | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C
Circuit No. 1 | Conductor | A | 1.2685 | 1.058 | 1.0581 | 0.96265 | 0.91709 | 0.93196 | 1.1613 | 1.058 | 1.0581 | 0.96265 | 0.91709 | 0.93196 | 1.1598 | 1.058 | 1.0581 | 0.96265 | 0.91709 | 0.93196
|  | B | 1.058 | 1.2685 | 1.0585 | 1.0365 | 0.96265 | 0.98023 | 1.058 | 1.1613 | 1.0585 | 1.0365 | 0.96265 | 0.98023 | 1.058 | 1.1598 | 1.0585 | 1.0365 | 0.96265 | 0.98023
|  | C | 1.0581 | 1.0585 | 1.2685 | 0.98023 | 0.93196 | 0.96305 | 1.0581 | 1.0585 | 1.1613 | 0.98023 | 0.93196 | 0.96305 | 1.0581 | 1.0585 | 1.1598 | 0.98023 | 0.93196 | 0.96305
Circuit No. 2 |  | A | 0.96265 | 1.0365 | 0.98023 | 1.2685 | 1.058 | 1.0585 | 0.96265 | 1.0365 | 0.98023 | 1.1613 | 1.058 | 1.0585 | 0.96265 | 1.0365 | 0.98023 | 1.1598 | 1.058 | 1.0585
|  | B | 0.91709 | 0.96265 | 0.93196 | 1.058 | 1.2685 | 1.0581 | 0.91709 | 0.96265 | 0.93196 | 1.058 | 1.1613 | 1.0581 | 0.91709 | 0.96265 | 0.93196 | 1.058 | 1.1598 | 1.0581
|  | C | 0.93196 | 0.98023 | 0.96305 | 1.0585 | 1.0581 | 1.2685 | 0.93196 | 0.98023 | 0.96305 | 1.0585 | 1.0581 | 1.1613 | 0.93196 | 0.98023 | 0.96305 | 1.0585 | 1.0581 | 1.1598
Circuit No. 1 | Sheath | A | 1.1613 | 1.058 | 1.0581 | 0.96265 | 0.91709 | 0.93196 | 1.1613 | 1.058 | 1.0581 | 0.96265 | 0.91709 | 0.93196 | 1.1598 | 1.058 | 1.0581 | 0.96265 | 0.91709 | 0.93196
|  | B | 1.058 | 1.1613 | 1.0585 | 1.0365 | 0.96265 | 0.98023 | 1.058 | 1.1613 | 1.0585 | 1.0365 | 0.96265 | 0.98023 | 1.058 | 1.1598 | 1.0585 | 1.0365 | 0.96265 | 0.98023
|  | C | 1.0581 | 1.0585 | 1.1613 | 0.98023 | 0.93196 | 0.96305 | 1.0581 | 1.0585 | 1.1613 | 0.98023 | 0.93196 | 0.96305 | 1.0581 | 1.0585 | 1.1598 | 0.98023 | 0.93196 | 0.96305
Circuit No. 2 |  | A | 0.96265 | 1.0365 | 0.98023 | 1.1613 | 1.058 | 1.0585 | 0.96265 | 1.0365 | 0.98023 | 1.1613 | 1.058 | 1.0585 | 0.96265 | 1.0365 | 0.98023 | 1.1598 | 1.058 | 1.0585
|  | B | 0.91709 | 0.96265 | 0.93196 | 1.058 | 1.1613 | 1.0581 | 0.91709 | 0.96265 | 0.93196 | 1.058 | 1.1613 | 1.0581 | 0.91709 | 0.96265 | 0.93196 | 1.058 | 1.1598 | 1.0581
|  | C | 0.93196 | 0.98023 | 0.96305 | 1.0585 | 1.0581 | 1.1613 | 0.93196 | 0.98023 | 0.96305 | 1.0585 | 1.0581 | 1.1613 | 0.93196 | 0.98023 | 0.96305 | 1.0585 | 1.0581 | 1.1598
Circuit No. 1 | Concentric neutral Skid wires | A | 1.1598 | 1.058 | 1.0581 | 0.96265 | 0.91709 | 0.93196 | 1.1598 | 1.058 | 1.0581 | 0.96265 | 0.91709 | 0.93196 | 1.1632 | 1.058 | 1.0581 | 0.96265 | 0.91709 | 0.93196
|  | B | 1.058 | 1.1598 | 1.0585 | 1.0365 | 0.96265 | 0.98023 | 1.058 | 1.1598 | 1.0585 | 1.0365 | 0.96265 | 0.98023 | 1.058 | 1.1632 | 1.0585 | 1.0365 | 0.96265 | 0.98023
|  | C | 1.0581 | 1.0585 | 1.1598 | 0.98023 | 0.93196 | 0.96305 | 1.0581 | 1.0585 | 1.1598 | 0.98023 | 0.93196 | 0.96305 | 1.0581 | 1.0585 | 1.1632 | 0.98023 | 0.93196 | 0.96305
Circuit No. 2 |  | A | 0.96265 | 1.0365 | 0.98023 | 1.1598 | 1.058 | 1.0585 | 0.96265 | 1.0365 | 0.98023 | 1.1598 | 1.058 | 1.0585 | 0.96265 | 1.0365 | 0.98023 | 1.1632 | 1.058 | 1.0585
|  | B | 0.91709 | 0.96265 | 0.93196 | 1.058 | 1.1598 | 1.0581 | 0.91709 | 0.96265 | 0.93196 | 1.058 | 1.1598 | 1.0581 | 0.91709 | 0.96265 | 0.93196 | 1.058 | 1.1632 | 1.0581
|  | C | 0.93196 | 0.98023 | 0.96305 | 1.0585 | 1.0581 | 1.1598 | 0.93196 | 0.98023 | 0.96305 | 1.0585 | 1.0581 | 1.1598 | 0.93196 | 0.98023 | 0.96305 | 1.0585 | 1.0581 | 1.1632
R Bonding [Ω/mile]
|  |  | Circuit No. 1 |  |  | Circuit No. 2
Conductor
|  | Phase | A | B | C | A | B | C
Circuit No. 1 | Conductor | A | 0.11603 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.11603 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.11603 | 0.095302 | 0.095302 | 0.095302
Circuit No. 2 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.11603 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11603 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11603
X Bonding [Ω/mile]
|  |  | Circuit No. 1 |  |  | Circuit No. 2
Conductor
|  | Phase | A | B | C | A | B | C
Circuit No. 1 | Conductor | A | 1.2685 | 1.058 | 1.0581 | 0.96265 | 0.91709 | 0.93196
|  | B | 1.058 | 1.2685 | 1.0585 | 1.0365 | 0.96265 | 0.98023
|  | C | 1.0581 | 1.0585 | 1.2685 | 0.98023 | 0.93196 | 0.96305
Circuit No. 2 |  | A | 0.96265 | 1.0365 | 0.98023 | 1.2685 | 1.058 | 1.0585
|  | B | 0.91709 | 0.96265 | 0.93196 | 1.058 | 1.2685 | 1.0581
|  | C | 0.93196 | 0.98023 | 0.96305 | 1.0585 | 1.0581 | 1.2685
R Phase [Ω/mile]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | A | B | C | A | B | C
Circuit No. 1 | A | 0.11603 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.11603 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| C | 0.095302 | 0.095302 | 0.11603 | 0.095302 | 0.095302 | 0.095302
Circuit No. 2 | A | 0.095302 | 0.095302 | 0.095302 | 0.11603 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11603 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11603
X Phase [Ω/mile]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | A | B | C | A | B | C
Circuit No. 1 | A | 1.2685 | 1.058 | 1.0581 | 0.96265 | 0.91709 | 0.93196
| B | 1.058 | 1.2685 | 1.0585 | 1.0365 | 0.96265 | 0.98023
| C | 1.0581 | 1.0585 | 1.2685 | 0.98023 | 0.93196 | 0.96305
Circuit No. 2 | A | 0.96265 | 1.0365 | 0.98023 | 1.2685 | 1.058 | 1.0585
| B | 0.91709 | 0.96265 | 0.93196 | 1.058 | 1.2685 | 1.0581
| C | 0.93196 | 0.98023 | 0.96305 | 1.0585 | 1.0581 | 1.2685
R Circuit [Ω/mile]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | A | B | C | A | B | C
Circuit No. 1 | A | 0.11603 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.11603 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| C | 0.095302 | 0.095302 | 0.11603 | 0.095302 | 0.095302 | 0.095302
Circuit No. 2 | A | 0.095302 | 0.095302 | 0.095302 | 0.11603 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11603 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11603
X Circuit [Ω/mile]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | A | B | C | A | B | C
Circuit No. 1 | A | 1.2685 | 1.058 | 1.0581 | 0.96265 | 0.91709 | 0.93196
| B | 1.058 | 1.2685 | 1.0585 | 1.0365 | 0.96265 | 0.98023
| C | 1.0581 | 1.0585 | 1.2685 | 0.98023 | 0.93196 | 0.96305
Circuit No. 2 | A | 0.96265 | 1.0365 | 0.98023 | 1.2685 | 1.058 | 1.0585
| B | 0.91709 | 0.96265 | 0.93196 | 1.058 | 1.2685 | 1.0581
| C | 0.93196 | 0.98023 | 0.96305 | 1.0585 | 1.0581 | 1.2685
R Sequence [Ω/mile]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | 0 | 1 | 2 | 0 | 1 | 2
Circuit No. 1 | 0 | 0.30663 | -1.9e-05 | 1.9e-05 | 0.28591 | -0.018343 | 0.018343
| 1 | 1.9e-05 | 0.020729 | 3.8e-05 | -0.030054 | -0.006593 | -0.012055
| 2 | -1.9e-05 | -3.8e-05 | 0.020729 | 0.030054 | 0.012055 | 0.006593
Circuit No. 2 | 0 | 0.28591 | 0.030054 | -0.030054 | 0.30663 | -0.000146 | 0.000146
| 1 | 0.018343 | 0.006593 | -0.012055 | 0.000146 | 0.020729 | 0.000291
| 2 | -0.018343 | 0.012055 | -0.006593 | -0.000146 | -0.000291 | 0.020729
X Sequence [Ω/mile]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | 0 | 1 | 2 | 0 | 1 | 2
Circuit No. 1 | 0 | 3.3848 | -0.000157 | -0.000157 | 2.8888 | 0.045293 | 0.045293
| 1 | -0.000157 | 0.21026 | 0.000314 | -0.038532 | -0.000205 | -0.00696
| 2 | -0.000157 | 0.000314 | 0.21026 | -0.038532 | -0.00696 | -0.000205
Circuit No. 2 | 0 | 2.8888 | -0.038532 | -0.038532 | 3.3848 | 6.2e-05 | 6.2e-05
| 1 | 0.045293 | -0.000205 | -0.00696 | 6.2e-05 | 0.21026 | -0.000124
| 2 | 0.045293 | -0.00696 | -0.000205 | 6.2e-05 | -0.000124 | 0.21026
R Sequence/R1
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | 0 | 1 | 2 | 0 | 1 | 2
Circuit No. 1 | 0 | 14.7923 | 0.000919 | 0.000919 | 13.7923 | 0.88489 | 0.88489
| 1 | 0.000919 | 1 | 0.001838 | 1.4498 | 0.31805 | 0.58156
| 2 | 0.000919 | 0.001838 | 1 | 1.4498 | 0.58156 | 0.31805
Circuit No. 2 | 0 | 13.7923 | 1.4498 | 1.4498 | 14.7923 | 0.007026 | 0.007026
| 1 | 0.88489 | 0.31805 | 0.58156 | 0.007026 | 1 | 0.014052
| 2 | 0.88489 | 0.58156 | 0.31805 | 0.007026 | 0.014052 | 1
X Sequence/X1
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | 0 | 1 | 2 | 0 | 1 | 2
Circuit No. 1 | 0 | 16.0984 | 0.000748 | 0.000748 | 13.739 | 0.21542 | 0.21542
| 1 | 0.000748 | 1 | 0.001495 | 0.18326 | 0.000973 | 0.033103
| 2 | 0.000748 | 0.001495 | 1 | 0.18326 | 0.033103 | 0.000973
Circuit No. 2 | 0 | 13.739 | 0.18326 | 0.18326 | 16.0984 | 0.000295 | 0.000295
| 1 | 0.21542 | 0.000973 | 0.033103 | 0.000295 | 1 | 0.000591
| 2 | 0.21542 | 0.033103 | 0.000973 | 0.000295 | 0.000591 | 1
Symmetrical Components [Ω/mile] | bar: Circuit No. 1 0 to Circuit No. 1 2
Circuit | Z0 | Circuit No. 1 0: Z1; Circuit No. 1 1: Z2; Circuit No. 1 2: ZOM(1,2)
1 | 0.306634 + j 3.384848 | Circuit No. 1 0: 0.020729 + j 0.21026; Circuit No. 1 1: 0.020729 + j 0.21026; Circuit No. 1 2: 0.285905 + j 2.888761
2 | 0.306634 + j 3.384848 | Circuit No. 1 0: 0.020729 + j 0.21026; Circuit No. 1 1: 0.020729 + j 0.21026; Circuit No. 1 2: 0.285905 + j 2.888761
Y Primitive [µS/mile] | bar: Circuit No. 1 0 to Circuit No. 2 0
Circuit No. 1 |  | Circuit No. 1 1: Circuit No. 2
A | B | C | A | B | C
0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781
Y Circuit [µS/mile] | bar: Circuit No. 1 0 to Circuit No. 2 0
Circuit No. 1 |  | Circuit No. 1 1: Circuit No. 2
A | B | C | A | B | C
0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781
Y Sequence [µS/mile] | bar: Circuit No. 1 0 to Circuit No. 2 0
Circuit No. 1 |  | Circuit No. 1 1: Circuit No. 2
0 | 1 | 2 | 0 | 1 | 2
0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781 | 0.16273 + j 162.729781

## Electrical Parameters
Electrical Parameters
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | CAYUGA air filled Oct 30 2025
Date: |  | 1/8/2026 1:58:20 PM
No. | Description |  | Unit | Cable No.1 | Cable No.2 | Cable No.3 | Cable No.4 | Cable No.5 | Cable No.6
1 | Cable Equipment ID |  |  | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL
Resistances
2 | DC Resistance of the conductor at 20°C |  | [Ω/mile] | 0.011162 | 0.011162 | 0.011162 | 0.011162 | 0.011162 | 0.011162
DC Resistance of the conductor at 20°C Equation
3 | DC Resistance of Conductor at Operating Temperature |  | [Ω/mile] | 0.013477 | 0.013477 | 0.013477 | 0.013477 | 0.013477 | 0.013477
DC Resistance of Conductor at Operating Temperature Equation
4 | AC Resistance of Conductor at 20°C |  | [Ω/mile] | 0.018776 | 0.018776 | 0.018776 | 0.018776 | 0.018776 | 0.018776
5 | AC Resistance of Conductor at Operating Temperature |  | [Ω/mile] | 0.020729 | 0.020729 | 0.020729 | 0.020729 | 0.020729 | 0.020729
AC Resistance of Conductor at Operating Temperature Equation
6 | DC Resistance of Sheath at 20°C |  | [Ω/mile] | 0.58591 | 0.58591 | 0.58591 | 0.58591 | 0.58591 | 0.58591
7 | DC Resistance of Sheath at Operating Temperature |  | [Ω/mile] | 0.68997 | 0.68997 | 0.68997 | 0.68997 | 0.68997 | 0.68997
DC Resistance of Sheath at Operating Temperature Equation
8 | DC Resistance of Concentric Wires at 20°C |  | [Ω/mile] | 20.0557 | 20.0557 | 20.0557 | 20.0557 | 20.0557 | 20.0557
9 | DC Resistance of Concentric Wires at Operating Temperature |  | [Ω/mile] | 23.6178 | 23.6178 | 23.6178 | 23.6178 | 23.6178 | 23.6178
DC Resistance of Concentric Wires at Operating Temperature Equation
Losses
10 | Conductor Losses |  | [W/ft] | 6.513 | 6.513 | 6.513 | 6.513 | 6.513 | 6.513
Conductor Losses Equation
11 | Dielectric Losses |  | [W/ft] | 0.54297 | 0.54297 | 0.54297 | 0.54297 | 0.54297 | 0.54297
Dielectric Losses Equation
12 | Metallic Screen Losses |  | [W/ft] | 0.98351 | 0.98351 | 0.98351 | 0.98351 | 0.98351 | 0.98351
Metallic Screen Losses Equation
13 | Armor/Pipe Losses |  | [W/ft] | 0 | 0 | 0 | 0 | 0 | 0
Armor/Pipe Losses Equation
14 | Total Losses |  | [W/ft] | 8.0395 | 8.0395 | 8.0395 | 8.0395 | 8.0395 | 8.0395
Total Losses Equation
Capacitance, Inductance, Impedance
15 | Capacitance |  | [µF/mile] | 0.4313 | 0.4313 | 0.4313 | 0.4313 | 0.4313 | 0.4313
Capacitance Equation
16 | Inductance of Conductor |  | [mH/mile] | 0.55756 | 0.55756 | 0.55756 | 0.55756 | 0.55756 | 0.55756
Inductance of Conductor Equation
17 | Reactance of Conductor |  | [Ω/mile] | 0.21019 | 0.21019 | 0.21019 | 0.21019 | 0.21019 | 0.21019
Reactance of Conductor Equation
18 | Inductance of Metallic Sheath |  | [mH/mile] | 0.27125 | 0.27125 | 0.27125 | 0.27125 | 0.27125 | 0.27125
Inductance of Metallic Sheath Equation
19 | Reactance of Metallic Sheath |  | [Ω/mile] | 0.10226 | 0.10226 | 0.10226 | 0.10226 | 0.10226 | 0.10226
Reactance of Metallic Sheath Equation
20 | Positive Sequence Impedance |  | [Ω/mile] | 0.020729 + j0.210194 | 0.020729 + j0.210194 | 0.020729 + j0.210194 | 0.020729 + j0.210194 | 0.020729 + j0.210194 | 0.020729 + j0.210194
Positive Sequence Impedance Equation
21 | Negative Sequence Impedance |  | [Ω/mile] | 0.020729 + j0.210194 | 0.020729 + j0.210194 | 0.020729 + j0.210194 | 0.020729 + j0.210194 | 0.020729 + j0.210194 | 0.020729 + j0.210194
Negative Sequence Impedance Equation
22 | Zero Sequence Impedance |  | [Ω/mile] | 0.601906 + j0.107934 | 0.601906 + j0.107934 | 0.601906 + j0.107934 | 0.601906 + j0.107934 | 0.601906 + j0.107934 | 0.601906 + j0.107934
Zero Sequence Impedance Equation
23 | Surge Impedance |  | [Ω] | 35.9563 | 35.9563 | 35.9563 | 35.9563 | 35.9563 | 35.9563
Surge Impedance Equation
Others
24 | Dielectric Stress at Insulation Inner Surface |  | [kV/in] | 192.0593 | 192.0593 | 192.0593 | 192.0593 | 192.0593 | 192.0593
Dielectric Stress at Insulation Inner Surface Equation
25 | Dielectric Stress at Insulation Outer Surface |  | [kV/in] | 114.3782 | 114.3782 | 114.3782 | 114.3782 | 114.3782 | 114.3782
26 | Insulation Resistance at 60°F (15.8°C) |  | [㏁.1000ft] | 418.235 | 418.235 | 418.235 | 418.235 | 418.235 | 418.235
Insulation Resistance at 60°F (15.8°C) Equation
27 | Reduction Factor (2pt bonded & single metallic screen) |  |  | n/a | n/a | n/a | n/a | n/a | n/a
Reduction Factor Equation (2pt bonded & single metallic screen)
28 | Charging Current for One Cable (Phase) |  | [A/mile] | 21.5893 | 21.5893 | 21.5893 | 21.5893 | 21.5893 | 21.5893
Charging Current Equation for One Cable (Phase)
29 | Charging Capacity of three phase system at Uo |  | [kvar/mile] | 8600.5667 | 8600.5667 | 8600.5667 | 8600.5667 | 8600.5667 | 8600.5667
Charging Capacity of three phase system at Uo Equation
30 | Voltage drop for Three Phase System |  | [V/A/mile] | 0.035904 | 0.035904 | 0.035904 | 0.035904 | 0.035904 | 0.035904
Voltage drop Equation for Three Phase System
31 | Induced Voltage (standing) on Sheath |  | [V/mile] | 182.5291 | 97.1557 | 151.1998 | 97.1557 | 182.5291 | 151.1998
32 | Induced Voltage angle on Sheath |  | [°] | -35.147 | 49.6866 | -129.2114 | 10.3134 | 95.147 | -170.7886
33 | Induced Voltage (standing) on Concentric Wires |  | [V/mile] | 180.6829 | 95.7497 | 149.4681 | 95.7497 | 180.6829 | 149.4681
34 | Induced Voltage angle on Concentric Wires |  | [°] | -35.1997 | 48.9689 | -128.9592 | 11.0311 | 95.1997 | -171.0408
35 | Induced current on Metallic Screen |  | [A] | 0 | 0 | 0 | 0 | 0 | 0
Induced current on Metallic Screen Equation

## Steady State
Cable Parameters under Normal Operation
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | CAYUGA air filled Oct 30 2025
Date: |  | 1/8/2026 1:58:20 PM
No. | Symbol | Description | Unit | Cable No.1 | Cable No.2 | Cable No.3 | Cable No.4 | Cable No.5 | Cable No.6
1 |  | Cable Equipment ID |  | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL | CAYUGA 230KV 5000 KCMIL
Normal Operation IEC 60287-1-1
Conductor AC Resistance
2 | R₀ | DC Resistance of the conductor at 20°C | [Ω/mile] | 0.011162 | 0.011162 | 0.011162 | 0.011162 | 0.011162 | 0.011162
DC Resistance of the conductor at 20°C Equation
3 | R' | DC Resistance of Conductor at Operating Temperature | [Ω/mile] | 0.013477 | 0.013477 | 0.013477 | 0.013477 | 0.013477 | 0.013477
DC Resistance of Conductor at Operating Temperature Equation
4 | dc | Conductor Diameter | [in] | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48
5 | s | Distance Between Conductor Axes | [in] | 5.4595 | 5.4595 | 5.4595 | 5.4595 | 5.4595 | 5.4595
6 | ks | Factor Used for xs Calculation (Skin Effect) |  | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62
7 | kp | Factor Used for xp Calculation (Proximity Effect) |  | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37
8 | Xs² | Component of Ys Calculation (Skin Effect) |  | 11.1648 | 11.1648 | 11.1648 | 11.1648 | 11.1648 | 11.1648
Component of Ys Calculation (Skin Effect) Equation
9 | Xp² | Component of Yp Calculation (Proximity Effect) |  | 6.6629 | 6.6629 | 6.6629 | 6.6629 | 6.6629 | 6.6629
Component of Yp Calculation (Proximity Effect) Equation
10 | ys | Skin Effect Factor |  | 0.43344 | 0.43344 | 0.43344 | 0.43344 | 0.43344 | 0.43344
Skin Effect Factor Equation
11 | yp | Proximity Effect Factor |  | 0.10474 | 0.10474 | 0.10474 | 0.10474 | 0.10474 | 0.10474
Proximity Effect Factor Equation
12 | R | AC Resistance of Conductor at Operating Temperature | [Ω/mile] | 0.020729 | 0.020729 | 0.020729 | 0.020729 | 0.020729 | 0.020729
AC Resistance of Conductor at Operating Temperature Equation
Dielectric Losses
13 | tanδ | Dielectric Loss Factor |  | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001
14 | ε | Insulation Relative Permittivity |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
15 | C | Cable Capacitance | [µF/mile] | 0.4313 | 0.4313 | 0.4313 | 0.4313 | 0.4313 | 0.4313
Cable Capacitance Equation
16 | U₀ | Voltage | [kV] | 132.7906 | 132.7906 | 132.7906 | 132.7906 | 132.7906 | 132.7906
17 | Wd | Cable Dielectric Losses Per Phase | [W/ft] | 0.54297 | 0.54297 | 0.54297 | 0.54297 | 0.54297 | 0.54297
Cable Dielectric Losses Per Phase Equation
Circulating Loss Factor
18 | ƛ'sa | Circulating Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
Circulating Loss Factor Equation
19 | ƛ'₁ | Screen Loss Factor Caused by Circulating Current |  | 0 | 0 | 0 | 0 | 0 | 0
Screen Loss Factor Equation
Eddy Loss Factor
20 | Rs | AC Resistance used for Eddy Loss Factor computation | [Ω/mile] | 0.68997 | 0.68997 | 0.68997 | 0.68997 | 0.68997 | 0.68997
21 | d | Mean diameter used for Eddy Loss Factor computation | [in] | 4.673 | 4.673 | 4.673 | 4.673 | 4.673 | 4.673
22 | ρs | Electrical Resistivity used for Eddy Loss Factor computation | [Ω.ft] | 6.6611e-08 | 6.6611e-08 | 6.6611e-08 | 6.6611e-08 | 6.6611e-08 | 6.6611e-08
23 | Ds | External diameter used for Eddy Loss Factor computation | [in] | 4.678 | 4.678 | 4.678 | 4.678 | 4.678 | 4.678
24 | ts | Thickness used for Eddy Loss Factor computation | [in] | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005
25 | β₁ | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 152.7522 | 152.7522 | 152.7522 | 152.7522 | 152.7522 | 152.7522
β₁ Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 Equation
26 | gs | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 1.0001 | 1.0001 | 1.0001 | 1.0001 | 1.0001 | 1.0001
gs Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 Equation
27 | m | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 0.087932 | 0.087932 | 0.087932 | 0.087932 | 0.087932 | 0.087932
m Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 Equation
28 | ƛ₀ | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 0.0042159 | 0.0042159 | 0.0042159 | 0.0042159 | 0.0042159 | 0.0042159
ƛ₁ Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 Equation
29 | Δ₁ | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 0.075981 | 0.075981 | 0.075981 | 0.075981 | 0.075981 | 0.075981
Δ₁ Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 Equation
30 | Δ₂ | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 0 | 0 | 0 | 0 | 0 | 0
Δ₂ Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 Equation
31 | F | Milliken conductor Effect |  | 1 | 1 | 1 | 1 | 1 | 1
Milliken conductor Effect Equation
32 | Fpipe | Magnetic effect factor due to pipe |  | 1 | 1 | 1 | 1 | 1 | 1
Magnetic effect factor due to pipe Equation
33 | Farmour | Magnetic effect factor due to armour |  | 1 | 1 | 1 | 1 | 1 | 1
Magnetic effect factor due to armour Equation
34 | ƛ''₁ | Screen Loss Factor Caused by Eddy Current |  | 0.15101 | 0.15101 | 0.15101 | 0.15101 | 0.15101 | 0.15101
Screen Loss Factor Caused by Eddy Current Equation
Metallic Screen Loss factor
35 | ƛ₁ | Screen Loss Factor |  | 0.15101 | 0.15101 | 0.15101 | 0.15101 | 0.15101 | 0.15101
Screen Loss Factor Equation
Armour and Pipe Loss Factor
36 | ƛ₂a | Armour Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
Armour Loss Factor Equation
37 | ƛ₂pipe | Pipe Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
Pipe Loss Factor Equation
38 | ƛ₂ | Armour Loss Factor + Pipe Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
Armour Loss Factor + Pipe Loss Factor Equation
Normal Operation IEC 60287-2-1
39 | T₁ | Thermal Resistance Between Conductor and Screen | [K.m/W] | 0.34068 | 0.34068 | 0.34068 | 0.34068 | 0.34068 | 0.34068
Thermal Resistance Between Conductor and Screen Equation
40 | t₁ | Insulation Thickness Between Conductor and Screen | [in] | 1.094 | 1.094 | 1.094 | 1.094 | 1.094 | 1.094
41 | ρTi | Thermal Resistivity of Insulation | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
42 | T₃ | Thermal Resistance of Jacket/Pipe Coating | [K.m/W] | 0.074098 | 0.074098 | 0.074098 | 0.074098 | 0.074098 | 0.074098
Thermal Resistance of Jacket/Pipe Coating Equation
43 | t₃ | Thickness of Jacket/Pipe Coating | [in] | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34
44 | ρTJ | Thermal Resistivity of Jacket/Pipe Coating | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
45 | T Conductor Shield | Thermal resistance | [K.m/W] | 0.029074 | 0.029074 | 0.029074 | 0.029074 | 0.029074 | 0.029074
46 |  | Thermal resistance equation
47 |  | Thermal resistivity | [K.m/W] | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
48 |  | Layer thickness | [in] | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094
49 |  | Internal diameter | [in] | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48
50 | T Insulation | Thermal resistance | [K.m/W] | 0.28871 | 0.28871 | 0.28871 | 0.28871 | 0.28871 | 0.28871
51 |  | Thermal resistance equation
52 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
53 |  | Layer thickness | [in] | 0.906 | 0.906 | 0.906 | 0.906 | 0.906 | 0.906
54 |  | Internal diameter | [in] | 2.668 | 2.668 | 2.668 | 2.668 | 2.668 | 2.668
55 | T Insulation Screen | Thermal resistance | [K.m/W] | 0.022899 | 0.022899 | 0.022899 | 0.022899 | 0.022899 | 0.022899
56 |  | Thermal resistance equation
57 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
58 |  | Layer thickness | [in] | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094
59 |  | Internal diameter | [in] | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48
60 | T Sheath | Thermal resistance | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
61 |  | Thermal resistance equation
62 |  | Thermal resistivity | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
63 |  | Layer thickness | [in] | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005
64 |  | Internal diameter | [in] | 4.668 | 4.668 | 4.668 | 4.668 | 4.668 | 4.668
65 | T Concentric wires | Thermal resistance | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
66 |  | Thermal resistance equation
67 |  | Thermal resistivity | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
68 |  | Layer thickness | [in] | 0.05076 | 0.05076 | 0.05076 | 0.05076 | 0.05076 | 0.05076
69 |  | Internal diameter | [in] | 4.678 | 4.678 | 4.678 | 4.678 | 4.678 | 4.678
70 | T Jacket | Thermal resistance | [K.m/W] | 0.074098 | 0.074098 | 0.074098 | 0.074098 | 0.074098 | 0.074098
71 |  | Thermal resistance equation
72 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
73 |  | Layer thickness | [in] | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34
74 |  | Internal diameter | [in] | 4.7795 | 4.7795 | 4.7795 | 4.7795 | 4.7795 | 4.7795
Thermal resistance of the external medium
75 | De / Do | External diameter of the cable conduit | [ft] | 0.45496 | 0.45496 | 0.45496 | 0.45496 | 0.45496 | 0.45496
76 | Z | Constant from IEC60287-2-1 clause 4.2.1 |  | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
77 | E | Constant from IEC60287-2-1 clause 4.2.1 |  | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25
78 | g | Constant from IEC60287-2-1 clause 4.2.1 |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
79 | h | Heat dissipation coefficient | [W/m²(K)⅘] | 2.2293 | 2.2293 | 2.2293 | 2.2293 | 2.2293 | 2.2293
Heat dissipation coefficient Equation
80 | Δθs | Temperature rise of the cable conduit surface above ambient | [°C] | 14.0115 | 14.0115 | 14.0115 | 14.0115 | 14.0115 | 14.0115
81 | T₄''' | Thermal resistance of the external medium | [K.m/W] | 0.53198 | 0.53198 | 0.53198 | 0.53198 | 0.53198 | 0.53198
Thermal resistance of the external medium Equation
Thermal Capacitance IEC 853-2
82 | Q Conductor | Thermal capacitance | [J/m.K] | 8747.9442 | 8747.9442 | 8747.9442 | 8747.9442 | 8747.9442 | 8747.9442
83 |  | Thermal capacitance equation
84 |  | Material surface | [in²] | 3.9302 | 3.9302 | 3.9302 | 3.9302 | 3.9302 | 3.9302
85 |  | Volumetric specific heat of the material | [J/(K*m³)] | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000
86 | Q Conductor Shield | Thermal capacitance | [J/m.K] | 1176.969 | 1176.969 | 1176.969 | 1176.969 | 1176.969 | 1176.969
87 |  | Thermal capacitance equation
88 |  | External diameter | [in] | 2.668 | 2.668 | 2.668 | 2.668 | 2.668 | 2.668
89 |  | Internal diameter | [in] | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48
90 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
91 | Q1 Insulation | Thermal capacitance | [J/m.K] | 5879.1234 | 5879.1234 | 5879.1234 | 5879.1234 | 5879.1234 | 5879.1234
92 |  | Thermal capacitance equation
93 |  | External diameter | [in] | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48
94 |  | Internal diameter | [in] | 2.668 | 2.668 | 2.668 | 2.668 | 2.668 | 2.668
95 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
96 | Q2 Insulation | Thermal capacitance | [J/m.K] | 9871.9913 | 9871.9913 | 9871.9913 | 9871.9913 | 9871.9913 | 9871.9913
97 |  | Thermal capacitance equation
98 |  | External diameter | [in] | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48
99 |  | Internal diameter | [in] | 2.668 | 2.668 | 2.668 | 2.668 | 2.668 | 2.668
100 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
101 | Q Insulation Screen | Thermal capacitance | [J/m.K] | 2091.4738 | 2091.4738 | 2091.4738 | 2091.4738 | 2091.4738 | 2091.4738
102 |  | Thermal capacitance equation
103 |  | External diameter | [in] | 4.668 | 4.668 | 4.668 | 4.668 | 4.668 | 4.668
104 |  | Internal diameter | [in] | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48
105 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
106 | Q Sheath | Thermal capacitance | [J/m.K] | 163.3798 | 163.3798 | 163.3798 | 163.3798 | 163.3798 | 163.3798
107 |  | Thermal capacitance equation
108 |  | External diameter | [in] | 4.678 | 4.678 | 4.678 | 4.678 | 4.678 | 4.678
109 |  | Internal diameter | [in] | 4.668 | 4.668 | 4.668 | 4.668 | 4.668 | 4.668
110 |  | Volumetric specific heat of the material | [J/(K*m³)] | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000
111 | Q Concentric wires | Thermal capacitance | [J/m.K] | 6.2441 | 6.2441 | 6.2441 | 6.2441 | 6.2441 | 6.2441
112 |  | Thermal capacitance equation
113 |  | Number of armour wires |  | 40 | 40 | 40 | 40 | 40 | 40
114 |  | Mean diameter of armour wire | [in] | 0.05076 | 0.05076 | 0.05076 | 0.05076 | 0.05076 | 0.05076
115 |  | Length of lay | [in] | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937
116 |  | Mean diameter of armour | [in] | 4.7288 | 4.7288 | 4.7288 | 4.7288 | 4.7288 | 4.7288
117 |  | Wire Shape is half-circle |  | 0 | 0 | 0 | 0 | 0 | 0
118 | Q Jacket | Thermal capacitance | [J/m.K] | 8467.1389 | 8467.1389 | 8467.1389 | 8467.1389 | 8467.1389 | 8467.1389
119 |  | Thermal capacitance equation
120 |  | External diameter | [in] | 5.4595 | 5.4595 | 5.4595 | 5.4595 | 5.4595 | 5.4595
121 |  | Internal diameter | [in] | 4.7795 | 4.7795 | 4.7795 | 4.7795 | 4.7795 | 4.7795
122 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
Ampacity
123 | T₄ | Total external thermal resistance | [K.m/W] | 0.53198 | 0.53198 | 0.53198 | 0.53198 | 0.53198 | 0.53198
Total external thermal resistance Equation
124 | Δθtr | Temperature rise of the air in the trough above the ambient temperature | [°C] | 13.2424 | 13.2424 | 13.2424 | 13.2424 | 13.2424 | 13.2424
125 | I | Cable core ampacity | [A] | 1288 | 1288 | 1288 | 1288 | 1288 | 1288
Cable core ampacity Equation

## Short Circuit
Cable Short Circuit
CYMCAP Version |  | 8.2 Revision 3
Study: |  | CAYUGA 230 KV
Execution: |  | CAYUGA air filled Oct 30 2025
Date: |  | 1/8/2026 1:58:20 PM
Symbol | Description |  | Unit | Circuit No. 1
| Cable Equipment ID |  |  | CAYUGA 230KV 5000 KCMIL
|  |  |  | Conductor |  |  | Sheath |  |  | Concentric neutral/Skid wires
|  |  |  | A | B | C | A | B | C | A | B | C
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2535.636 | 2535.636 | 2535.636 | 47.3569 | 47.3569 | 47.3569 | 52.2225 | 52.2225 | 52.2225
θi | Initial Temperature |  | [°C] | 72.7261 | 72.7261 | 72.7261 | 65.1445 | 65.1445 | 65.1445 | 65.1445 | 65.1445 | 65.1445
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 250 | 250 | 150 | 150 | 150 | 150 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1221253.4314 | 1221253.4314 | 1221253.4314 | 16875.1422 | 16875.1422 | 16875.1422 | 18608.9646 | 18608.9646 | 18608.9646
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1223134.3867 | 1223134.3867 | 1223134.3867 | 20983.1586 | 20983.1586 | 20983.1586 | 19074.5771 | 19074.5771 | 19074.5771
Symbol | Description |  | Unit | Circuit No. 2
| Cable Equipment ID |  |  | CAYUGA 230KV 5000 KCMIL
|  |  |  | Conductor |  |  | Sheath |  |  | Concentric neutral/Skid wires
|  |  |  | A | B | C | A | B | C | A | B | C
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2535.636 | 2535.636 | 2535.636 | 47.3569 | 47.3569 | 47.3569 | 52.2225 | 52.2225 | 52.2225
θi | Initial Temperature |  | [°C] | 72.7261 | 72.7261 | 72.7261 | 65.1445 | 65.1445 | 65.1445 | 65.1445 | 65.1445 | 65.1445
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 250 | 250 | 150 | 150 | 150 | 150 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1221253.4314 | 1221253.4314 | 1221253.4314 | 16875.1422 | 16875.1422 | 16875.1422 | 18608.9646 | 18608.9646 | 18608.9646
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1223134.3867 | 1223134.3867 | 1223134.3867 | 20983.1586 | 20983.1586 | 20983.1586 | 19074.5771 | 19074.5771 | 19074.5771