## Study Summary
Study Summary
CYMCAP Version |  | 8.2 Revision 3
Study: |  | HOMER CITY GENERATION
Execution: |  | Homer HDD January 2026
Date: |  | 1/6/2026 3:22:35 PM
General Simulation Data
Steady State Option | [8 empty] | Temperature
Consider Electrical interaction between circuits | [8 empty] | No
Induced currents in metallic layers as a fraction of conductor current (applied to all single phase circuits) : | [8 empty] | 0
Conductor Resistances Computation Option: | [8 empty] | IEC-228
Standard Settings Options
General guidance | [8 empty] | Custom
Factor on RAC due to magnetic armour | [8 empty] | CIGREGuidance
Factor on RAC due to magnetic duct | [8 empty] | CIGREGuidance
Factor on ƛ₁ due to magnetic armour | [8 empty] | CYMCAPGuidance
Factor on ƛ₁ due to magnetic duct | [8 empty] | CIGREGuidance
Factor on ƛ₂ due to ƛ'₁ | [8 empty] | CYMCAPGuidance
ƛ''₁ computation | [8 empty] | CIGREGuidance
ƛ₂pipe computation | [8 empty] | CYMCAPGuidance
Wd computation | [8 empty] | CIGREGuidance
T₂ computation | [8 empty] | CIGREGuidance
T₄ computation | [8 empty] | CYMCAPGuidance
Installation Type:Multiple Ductbanks/Backfills
Ambient Soil Temperature at Installation Depth [°C] | [8 empty] | 12.2
Native Soil Thermal Resistivity [K.m/W] | [8 empty] | 0.7
Consider Non-Isothermal Earth Surface | [8 empty] | No
Layer Name |  | X [ft] | Y [ft] | Width [ft] | Height [ft] | Thermal Resistivity [K.m/W]
NSTD DB1 |  | 0 | 25.0001 | 2.8806 | 2.8806 | 1.5
Native |  | 0 | 0.4165 | 50.0002 | 0.833 | 1.37
Results Summary
Cable No. | Cable ID | Circuit No. | Feeder ID | Cable Phase | Cable Frequency | Daily Load Factor | X coordinate [ft] | Y coordinate [ft] | Conductor temperature [°C] | Ampacity [A]
1 | HOMER CITY 345KV 5000KCMIL JULY | 1 |  | A | 60 | 1 | 0 | 24.3533 | 38.8548 | 529
2 | HOMER CITY 345KV 5000KCMIL JULY | 1 |  | B | 60 | 1 | 0.627 | 24.7152 | 39.272 | 529
3 | HOMER CITY 345KV 5000KCMIL JULY | 1 |  | C | 60 | 1 | 0.627 | 25.4393 | 39.9576 | 529
4 | HOMER CITY 345KV 5000KCMIL JULY | 2 |  | A | 60 | 1 | 0 | 25.8012 | 40.207 | 529
5 | HOMER CITY 345KV 5000KCMIL JULY | 2 |  | B | 60 | 1 | -0.627 | 25.4393 | 39.9559 | 529
6 | HOMER CITY 345KV 5000KCMIL JULY | 2 |  | C | 60 | 1 | -0.627 | 24.7152 | 39.2712 | 529

## Steady State Summary
Steady State Summary
CYMCAP Version |  | 8.2 Revision 3
Study: |  | HOMER CITY GENERATION
Execution: |  | Homer HDD January 2026
Date: |  | 1/6/2026 3:22:35 PM
Simulation Data
Installation type: |  | Multiple Ductbanks
Steady State Option |  | Temperature
Ambient temperature [°C] |  | 12.2
Native Soil Thermal Resistivity [K.m/W] |  | 0.7
Consider Non-Isothermal Earth Surface |  | No
Consider effect of soil dry out |  | No
Consider Electrical interaction between circuits |  | No
Induced current in metallic layers as a fraction of conductor current (applied to all single phase circuits) [A] |  | 0
Variable | Description |  | Unit | Cables
Cable No. | Cable Index Number |  |  | 1 | 2 | 3 | 4 | 5 | 6
General Input Data
Cable ID | Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY
Circuit No. | Circuit No. |  |  | 1 | 1 | 1 | 2 | 2 | 2
Phase | Cable Phase |  |  | A | B | C | A | B | C
Fq | Operating Frequency |  | [Hz] | 60 | 60 | 60 | 60 | 60 | 60
x | X coordinate |  | [ft] | 0 | 0.627 | 0.627 | 0 | -0.627 | -0.627
y | Y coordinate |  | [ft] | 24.3533 | 24.7152 | 25.4393 | 25.8012 | 25.4393 | 24.7152
DLF | Daily Load Factor |  | [p.u.] | bar: Cables 1 to Cables 6
| Bonding Type |  |  | 1 Conductor 1 Point Bonded Triangular | 1 Conductor 1 Point Bonded Triangular | 1 Conductor 1 Point Bonded Triangular | 1 Conductor 1 Point Bonded Triangular | 1 Conductor 1 Point Bonded Triangular | 1 Conductor 1 Point Bonded Triangular
Ampacity
I | Steady State Ampacity |  | [A] | 529 | 529 | 529 | 529 | 529 | 529
I₀ | Steady State Ampacity without insulation temperature drop constraint |  | [A] | n/a | n/a | n/a | n/a | n/a | n/a
Temperatures
θc | Conductor temperature |  | [°C] | 38.8548 | 39.272 | 39.9576 | 40.207 | 39.9559 | 39.2712
Δθins | Temperature drop across the insulation |  | [°C] | n/a | n/a | n/a | n/a | n/a | n/a
θs | Sheath/Shield temperature |  | [°C] | 36.9267 | 37.3428 | 38.0267 | 38.2755 | 38.025 | 37.342
θa | Armour temperature |  | [°C] | n/a | n/a | n/a | n/a | n/a | n/a
θsurf | Cable surface temperature |  | [°C] | 36.4672 | 36.8832 | 37.5668 | 37.8155 | 37.5652 | 36.8824
θduct | Duct surface temperature |  | [°C] | 34.3429 | 34.7631 | 35.4537 | 35.7048 | 35.452 | 34.7623
Resistances
R₀ | DC Resistance of the conductor at 20°C |  | [Ω/mile] | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119
R | AC Resistance of the Conductor at Operating Temperature |  | [Ω/mile] | 0.018648 | 0.018663 | 0.018688 | 0.018697 | 0.018688 | 0.018663
ys | Skin Effect Factor |  |  | 0.50617 | 0.50515 | 0.50347 | 0.50286 | 0.50347 | 0.50515
yp | Proximity Effect Factor |  |  | 0.045316 | 0.045255 | 0.045156 | 0.04512 | 0.045156 | 0.045256
Losses
Wc | Conductor Losses |  | [W/ft] | 0.98833 | 0.98914 | 0.99048 | 0.99097 | 0.99048 | 0.98914
Wd | Dielectric Losses |  | [W/ft] | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151
Ws | Metallic Screen Losses |  | [W/ft] | 0.10383 | 0.10367 | 0.10342 | 0.10333 | 0.10342 | 0.10367
Wa | Armor/Pipe Losses |  | [W/ft] | 0 | 0 | 0 | 0 | 0 | 0
Wt | Total Losses |  | [W/ft] | 2.0637 | 2.0643 | 2.0654 | 2.0658 | 2.0654 | 2.0643
ƛ₁ | Screen Loss Factor |  |  | 0.10505 | 0.10481 | 0.10441 | 0.10427 | 0.10441 | 0.10481
ƛ₂ | Armour Loss Factor + Pipe Loss Factor |  |  | 0 | 0 | 0 | 0 | 0 | 0
Thermal resistances
T1 | Thermal Resistance Between Conductor and Screen |  | [K.m/W] | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868
T2 | Thermal Resistance Between Screen and Armour |  | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
T3 | Thermal Resistance of the Jacket/Pipe Coating |  | [K.m/W] | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863
T4 | Total external thermal resistance |  | [K.m/W] | 3.5842 | 3.6445 | 3.7435 | 3.7795 | 3.7432 | 3.6444
Others
Δθint | Temperature rise due to surrounding heat sources |  | [°C] | 16.7305 | 17.1863 | 18.0032 | 18.3464 | 18.0017 | 17.1858
| Induced Voltage (standing) on Sheath |  | [V/mile] | 66.5477 | 66.5459 | 66.5459 | 66.5477 | 66.5459 | 66.5459
| Induced Voltage angle on Sheath |  | [°] | -30 | 89.9892 | -149.9892 | -30 | 89.9892 | -149.9892
| Induced Voltage (standing) on Concentric Wires |  | [V/mile] | 67.7081 | 67.7063 | 67.7063 | 67.7081 | 67.7063 | 67.7063
| Induced Voltage angle on Concentric Wires |  | [°] | -30 | 89.9893 | -149.9893 | -30 | 89.9893 | -149.9893
| Induced current on Metallic Screen |  | [A] | 0 | 0 | 0 | 0 | 0 | 0

## Cable - HO...5KV 5000KCMIL JULY
Cables Report
CYMCAP Version |  | 8.2 Revision 3
Study: |  | HOMER CITY GENERATION
Execution: |  | Homer HDD January 2026
Date: |  | 1/6/2026 3:22:35 PM
No. | Description |  | Unit | 1
General Cable Information
1 | Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
2 | Number of Cores |  |  | Single Core
3 | Voltage |  | [kV] | 345
4 | Conductor Area |  | [in²] | 3.9202
5 | Cable Overall Diameter |  | [in] | 6.0332
6 | Maximum Steady-State Conductor Temperature |  | [°C] | 90
7 | Maximum Emergency Conductor Temperature |  | [°C] | 110
Conductor
8 | Material |  |  | Copper
9 | Electrical Resistivity at 20°C |  | [µΩ.cm] | 1.7241
10 | Temperature Coefficient at 20°C |  | [1/K] | 0.00393
11 | Reciprocal of Temperature Coefficient of Resistance (BETA) |  | [K] | 234.4529
12 | Volumetric Specific Heat (SH) |  | [J/(K*cm³)] | 3.45
13 | Construction |  |  | 6 Segments
14 | Conductor Insulation System |  |  | Extruded
15 | Milliken Wires Construction |  |  | Bare Unidirectional Wires
16 | Ks (Skin Effect Coefficient) |  |  | 0.62
17 | Kp (Proximity Effect Coefficient) |  |  | 0.37
18 | Diameter |  | [in] | 2.48
Conductor Shield
19 | Thickness |  | [in] | 0.067
20 | Diameter |  | [in] | 2.614
Insulation
21 | Material |  |  | XLPE Unfilled
22 | Thermal Resistivity |  | [K.m/W] | 3.5
23 | Dielectric Loss Factor - ( tan delta ) |  |  | 0.001
24 | Relative Permittivity - ( epsilon ) |  |  | 2.5
25 | Specific Insulation Resistance Constant at 60°F - ( K ) |  | [㏁.1000ft] | 1858.0608
26 | Thickness |  | [in] | 1.201
27 | Diameter |  | [in] | 5.016
Insulation Screen
28 | Material |  |  | Semi Conducting Screen
29 | Thickness |  | [in] | 0.067
30 | Diameter |  | [in] | 5.15
Concentric neutral/Skid wires
31 | Are Concentric Neutral Wires Around Each Core? |  |  | n/a
32 | Material |  |  | Copper
33 | Electrical Resistivity at 20°C |  | [µΩ.cm] | 1.7241
34 | Temperature Coefficient at 20°C |  | [1/K] | 0.00393
35 | Reciprocal of Temperature Coefficient of Resistance (BETA) |  | [K] | 234.5
36 | Volumetric Specific Heat (SH) |  | [J/(K*cm³)] | 3.45
37 | Wire Type |  |  | Round Wires
38 | Length of Lay |  | [in] | 0.3937
39 | Number of Wires |  |  | 82
40 | Wire Gauge |  |  | Undefined
41 | Thickness |  | [in] | 0.090598
42 | Diameter |  | [in] | 5.3312
Sheath
43 | Is Sheath Around Each Core? |  |  | n/a
44 | Material |  |  | Copper
45 | Electrical Resistivity at 20°C |  | [µΩ.cm] | 1.7241
46 | Temperature Coefficient at 20°C |  | [1/K] | 0.00393
47 | Reciprocal of Temperature Coefficient of Resistance (BETA) |  | [K] | 234.5
48 | Volumetric Specific Heat (SH) |  | [J/(K*cm³)] | 3.45
49 | Corrugation Type |  |  | Non Corrugated
50 | Thickness |  | [in] | 0.005
51 | Diameter |  | [in] | 5.3412
Jacket
52 | Material |  |  | Polyethylene
53 | Thermal Resistivity |  | [K.m/W] | 3.5
54 | Thickness |  | [in] | 0.346
55 | Diameter |  | [in] | 6.0332
No. | Description |  | Unit | 1
Specific Installation Data
56 | Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
57 | Cable Frequency |  | [Hz] | 60
58 | Sheath / Shield Bonding |  |  | 1 Conductor 1 Point Bonded Triangular
59 | Loss Factor Constant (ALOS) |  |  | 0.3
60 | Spacing Between Cables in Section |  |  | n/a
61 | Conduit construction |  |  | PVC Duct in Concrete
62 | Conduit material thermal resistivity |  | [K.m/W] | 6
63 | Conduit filling material |  |  | Air
64 | Inner diameter of the conduit |  | [in] | 7.981
65 | Outer diameter of the conduit |  | [in] | 8.625
Cable ID : HOMER CITY 345KV 5000KCMIL JULY
Cable Title |  | HOMER CITY GEN 345KV 5000KCMIL July

## Steady State
Cable Parameters under Normal Operation
CYMCAP Version |  | 8.2 Revision 3
Study: |  | HOMER CITY GENERATION
Execution: |  | Homer HDD January 2026
Date: |  | 1/6/2026 3:22:35 PM
No. | Symbol | Description | Unit | Cable No.1 | Cable No.2 | Cable No.3 | Cable No.4 | Cable No.5 | Cable No.6
1 |  | Cable Equipment ID |  | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY
Normal Operation IEC 60287-1-1
Conductor AC Resistance
2 | R₀ | DC Resistance of the conductor at 20°C | [Ω/mile] | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119
DC Resistance of the conductor at 20°C Equation
3 | R' | DC Resistance of Conductor at Operating Temperature | [Ω/mile] | 0.012019 | 0.012038 | 0.012068 | 0.012079 | 0.012068 | 0.012038
DC Resistance of Conductor at Operating Temperature Equation
4 | dc | Conductor Diameter | [in] | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48
5 | s | Distance Between Conductor Axes | [in] | 8.6881 | 8.6881 | 8.6881 | 8.6881 | 8.6881 | 8.6881
6 | ks | Factor Used for xs Calculation (Skin Effect) |  | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62
7 | kp | Factor Used for xp Calculation (Proximity Effect) |  | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37
8 | Xs² | Component of Ys Calculation (Skin Effect) |  | 12.5186 | 12.4995 | 12.4683 | 12.457 | 12.4684 | 12.4996
Component of Ys Calculation (Skin Effect) Equation
9 | Xp² | Component of Yp Calculation (Proximity Effect) |  | 7.4708 | 7.4594 | 7.4408 | 7.434 | 7.4408 | 7.4594
Component of Yp Calculation (Proximity Effect) Equation
10 | ys | Skin Effect Factor |  | 0.50617 | 0.50515 | 0.50347 | 0.50286 | 0.50347 | 0.50515
Skin Effect Factor Equation
11 | yp | Proximity Effect Factor |  | 0.045316 | 0.045255 | 0.045156 | 0.04512 | 0.045156 | 0.045256
Proximity Effect Factor Equation
12 | R | AC Resistance of Conductor at Operating Temperature | [Ω/mile] | 0.018648 | 0.018663 | 0.018688 | 0.018697 | 0.018688 | 0.018663
AC Resistance of Conductor at Operating Temperature Equation
Dielectric Losses
13 | tanδ | Dielectric Loss Factor |  | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001
14 | ε | Insulation Relative Permittivity |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
15 | C | Cable Capacitance | [µF/mile] | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279
Cable Capacitance Equation
16 | U₀ | Voltage | [kV] | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858
17 | Wd | Cable Dielectric Losses Per Phase | [W/ft] | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151
Cable Dielectric Losses Per Phase Equation
Circulating Loss Factor
18 | ƛ'sa | Circulating Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
Circulating Loss Factor Equation
19 | ƛ'₁ | Screen Loss Factor Caused by Circulating Current |  | 0 | 0 | 0 | 0 | 0 | 0
Screen Loss Factor Equation
Eddy Loss Factor
20 | Rs | AC Resistance used for Eddy Loss Factor computation | [Ω/mile] | 0.54722 | 0.54806 | 0.54944 | 0.54994 | 0.54943 | 0.54806
21 | d | Mean diameter used for Eddy Loss Factor computation | [in] | 5.3362 | 5.3362 | 5.3362 | 5.3362 | 5.3362 | 5.3362
22 | ρs | Electrical Resistivity used for Eddy Loss Factor computation | [Ω.ft] | 6.0328e-08 | 6.042e-08 | 6.0571e-08 | 6.0627e-08 | 6.0571e-08 | 6.042e-08
23 | Ds | External diameter used for Eddy Loss Factor computation | [in] | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412
24 | ts | Thickness used for Eddy Loss Factor computation | [in] | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005
25 | β₁ | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 160.5108 | 160.3879 | 160.1865 | 160.1134 | 160.187 | 160.3882
β₁ Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 Equation
26 | gs | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 1.0001 | 1.0001 | 1.0001 | 1.0001 | 1.0001 | 1.0001
gs Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 Equation
27 | m | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 0.11087 | 0.1107 | 0.11042 | 0.11032 | 0.11042 | 0.1107
m Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 Equation
28 | ƛ₀ | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 0.0034356 | 0.0034252 | 0.0034083 | 0.0034021 | 0.0034083 | 0.0034253
ƛ₁ Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 Equation
29 | Δ₁ | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 0.041869 | 0.041875 | 0.041883 | 0.041886 | 0.041883 | 0.041875
Δ₁ Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 Equation
30 | Δ₂ | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 0 | 0 | 0 | 0 | 0 | 0
Δ₂ Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 Equation
31 | F | Milliken conductor Effect |  | 1 | 1 | 1 | 1 | 1 | 1
Milliken conductor Effect Equation
32 | Fpipe | Magnetic effect factor due to pipe |  | 1 | 1 | 1 | 1 | 1 | 1
Magnetic effect factor due to pipe Equation
33 | Farmour | Magnetic effect factor due to armour |  | 1 | 1 | 1 | 1 | 1 | 1
Magnetic effect factor due to armour Equation
34 | ƛ''₁ | Screen Loss Factor Caused by Eddy Current |  | 0.10505 | 0.10481 | 0.10441 | 0.10427 | 0.10441 | 0.10481
Screen Loss Factor Caused by Eddy Current Equation
Metallic Screen Loss factor
35 | ƛ₁ | Screen Loss Factor |  | 0.10505 | 0.10481 | 0.10441 | 0.10427 | 0.10441 | 0.10481
Screen Loss Factor Equation
Armour and Pipe Loss Factor
36 | ƛ₂a | Armour Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
Armour Loss Factor Equation
37 | ƛ₂pipe | Pipe Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
Pipe Loss Factor Equation
38 | ƛ₂ | Armour Loss Factor + Pipe Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
Armour Loss Factor + Pipe Loss Factor Equation
Normal Operation IEC 60287-2-1
39 | T₁ | Thermal Resistance Between Conductor and Screen | [K.m/W] | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868
Thermal Resistance Between Conductor and Screen Equation
40 | t₁ | Insulation Thickness Between Conductor and Screen | [in] | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335
41 | ρTi | Thermal Resistivity of Insulation | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
42 | T₃ | Thermal Resistance of Jacket/Pipe Coating | [K.m/W] | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863
Thermal Resistance of Jacket/Pipe Coating Equation
43 | t₃ | Thickness of Jacket/Pipe Coating | [in] | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346
44 | ρTJ | Thermal Resistivity of Jacket/Pipe Coating | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
45 | T Conductor Shield | Thermal resistance | [K.m/W] | 0.020938 | 0.020938 | 0.020938 | 0.020938 | 0.020938 | 0.020938
46 |  | Thermal resistance equation
47 |  | Thermal resistivity | [K.m/W] | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
48 |  | Layer thickness | [in] | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067
49 |  | Internal diameter | [in] | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48
50 | T Insulation | Thermal resistance | [K.m/W] | 0.36305 | 0.36305 | 0.36305 | 0.36305 | 0.36305 | 0.36305
51 |  | Thermal resistance equation
52 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
53 |  | Layer thickness | [in] | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201
54 |  | Internal diameter | [in] | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614
55 | T Insulation Screen | Thermal resistance | [K.m/W] | 0.014686 | 0.014686 | 0.014686 | 0.014686 | 0.014686 | 0.014686
56 |  | Thermal resistance equation
57 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
58 |  | Layer thickness | [in] | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067
59 |  | Internal diameter | [in] | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016
60 | T Concentric wires | Thermal resistance | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
61 |  | Thermal resistance equation
62 |  | Thermal resistivity | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
63 |  | Layer thickness | [in] | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906
64 |  | Internal diameter | [in] | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15
65 | T Sheath | Thermal resistance | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
66 |  | Thermal resistance equation
67 |  | Thermal resistivity | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
68 |  | Layer thickness | [in] | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001
69 |  | Internal diameter | [in] | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312
70 | T Jacket | Thermal resistance | [K.m/W] | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863
71 |  | Thermal resistance equation
72 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
73 |  | Layer thickness | [in] | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346
74 |  | Internal diameter | [in] | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412
Thermal resistance inside the duct
75 | U | Constant from IEC6028721 clause4272 |  | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87
76 | V | Constant from IEC6028721 clause4272 |  | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312
77 | Y | Constant from IEC6028721 clause4272 |  | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037
78 | θm | Mean temperature of the medium in conduit | [°C] | 35.6559 | 36.0741 | 36.7613 | 37.0113 | 36.7596 | 36.0733
79 | Deq | Equivalent diameter of the cables inside the conduit | [in] | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332
80 | T₄' | Thermal resistance of the medium in conduit | [K.m/W] | 0.23966 | 0.23893 | 0.23775 | 0.23732 | 0.23775 | 0.23893
Thermal resistance of the medium in conduit Equation
Thermal resistance of the duct
81 | Do | Outer diameter of the conduit | [in] | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625
82 | Di | Inner diameter of the conduit | [in] | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981
83 | ρT | Thermal resistivity of the conduit material | [K.m/W] | 6 | 6 | 6 | 6 | 6 | 6
84 | T₄'' | Thermal resistance of the conduit | [K.m/W] | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104
Thermal resistance of the conduit Equation
Thermal resistance of the external medium
85 | L | Depth of cable/conduit axis | [ft] | 24.3533 | 24.7152 | 25.4393 | 25.8012 | 25.4393 | 24.7152
86 | De / Do | External diameter of the cable conduit | [ft] | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875
87 | u | Geometric factor as per IEC60287-2-1 clause 4.2.2 |  | 67.7658 | 68.7728 | 70.7876 | 71.7946 | 70.7876 | 68.7728
Geometric factor Equation as per IEC60287-2-1 clause 4.2.2
88 | ρTs | Thermal resistivity of the soil | [K.m/W] | 1.0231 | 1.0131 | 0.98297 | 0.96283 | 0.98294 | 1.013
89 | T₄'''self | Thermal resistance of the cable isolated | [K.m/W] | 0.79938 | 0.79389 | 0.77483 | 0.76112 | 0.77482 | 0.79384
Thermal resistance of the cable isolated Equation
90 | T₄'''mutual | Thermal resistance associated to the temperature rise due to surrounding heat sources | [K.m/W] | 2.4711 | 2.5376 | 2.6568 | 2.7069 | 2.6566 | 2.5375
Thermal resistance associated to the temperature rise due to surrounding heat sources Equation
91 | Δθint | Temperature rise due to surrounding heat sources | [°C] | 16.7305 | 17.1863 | 18.0032 | 18.3464 | 18.0017 | 17.1858
Temperature rise due to surrounding heat sources Equation
92 | T₄''' | Thermal resistance of the external medium | [K.m/W] | 3.2704 | 3.3315 | 3.4316 | 3.468 | 3.4314 | 3.3313
Thermal resistance of the external medium Equation
Thermal Capacitance IEC 853-2
93 | Q Conductor | Thermal capacitance | [J/m.K] | 8725.6848 | 8725.6848 | 8725.6848 | 8725.6848 | 8725.6848 | 8725.6848
94 |  | Thermal capacitance equation
95 |  | Material surface | [in²] | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202
96 |  | Volumetric specific heat of the material | [J/(K*m³)] | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000
97 | Q Conductor Shield | Thermal capacitance | [J/m.K] | 830.1027 | 830.1027 | 830.1027 | 830.1027 | 830.1027 | 830.1027
98 |  | Thermal capacitance equation
99 |  | External diameter | [in] | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614
100 |  | Internal diameter | [in] | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48
101 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
102 | Q1 Insulation | Thermal capacitance | [J/m.K] | 7635.6685 | 7635.6685 | 7635.6685 | 7635.6685 | 7635.6685 | 7635.6685
103 |  | Thermal capacitance equation
104 |  | External diameter | [in] | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016
105 |  | Internal diameter | [in] | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614
106 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
107 | Q2 Insulation | Thermal capacitance | [J/m.K] | 14652.0704 | 14652.0704 | 14652.0704 | 14652.0704 | 14652.0704 | 14652.0704
108 |  | Thermal capacitance equation
109 |  | External diameter | [in] | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016
110 |  | Internal diameter | [in] | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614
111 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
112 | Q Insulation Screen | Thermal capacitance | [J/m.K] | 1656.624 | 1656.624 | 1656.624 | 1656.624 | 1656.624 | 1656.624
113 |  | Thermal capacitance equation
114 |  | External diameter | [in] | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15
115 |  | Internal diameter | [in] | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016
116 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
117 | Q Concentric wires | Thermal capacitance | [J/m.K] | 42.9278 | 42.9278 | 42.9278 | 42.9278 | 42.9278 | 42.9278
118 |  | Thermal capacitance equation
119 |  | Number of armour wires |  | 82 | 82 | 82 | 82 | 82 | 82
120 |  | Mean diameter of armour wire | [in] | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598
121 |  | Length of lay | [in] | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937
122 |  | Mean diameter of armour | [in] | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406
123 |  | Wire Shape is half-circle |  | 0 | 0 | 0 | 0 | 0 | 0
124 | Q Sheath | Thermal capacitance | [J/m.K] | 186.5724 | 186.5724 | 186.5724 | 186.5724 | 186.5724 | 186.5724
125 |  | Thermal capacitance equation
126 |  | External diameter | [in] | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412
127 |  | Internal diameter | [in] | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312
128 |  | Volumetric specific heat of the material | [J/(K*m³)] | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000
129 | Q Jacket | Thermal capacitance | [J/m.K] | 9572.009 | 9572.009 | 9572.009 | 9572.009 | 9572.009 | 9572.009
130 |  | Thermal capacitance equation
131 |  | External diameter | [in] | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332
132 |  | Internal diameter | [in] | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412
133 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
Ampacity
134 | T₄ | Total external thermal resistance | [K.m/W] | 3.5842 | 3.6445 | 3.7435 | 3.7795 | 3.7432 | 3.6444
Total external thermal resistance Equation
135 | I | Cable core ampacity | [A] | 529 | 529 | 529 | 529 | 529 | 529
Cable core ampacity Equation