## General Su...ITY GENERATION-141
General Summary Report
CYMCAP Version |  | 8.2 Revision 3
Study: |  | HOMER CITY GENERATION
Execution: |  | Three Units Deepest Depth 12 31
Date: |  | 1/8/2026 12:32:16 PM
Simulation Data
Installation type: |  | Multiple Ductbanks
Steady State Option |  | Temperature
Ambient temperature [°C] |  | 19.4
Native Soil Thermal Resistivity [K.m/W] |  | 1.3
Consider Non-Isothermal Earth Surface |  | No
Consider effect of soil dry out |  | No
Consider Electrical interaction between circuits |  | No
Induced current in metallic layers as a fraction of conductor current (applied to all single phase circuits) [A] |  | 0
Installation Type:Multiple Ductbanks/Backfills
Ambient Soil Temperature at Installation Depth [°C] |  | 19.4
Native Soil Thermal Resistivity [K.m/W] |  | 1.3
Consider Non-Isothermal Earth Surface |  | No
Layer Name |  | X [ft] | Y [ft] | Width [ft] | Height [ft] | Thermal Resistivity [K.m/W]
Unit 3000 |  | 4.5112e-05 | 6.25 | 27.5001 | 2.5 | 0.6
Surface Ag |  | 0 | 0.75 | 29.5001 | 1.5 | 5
Gravel Bed |  | 0 | 7.75 | 27.5001 | 0.5 | 5
Backfill |  | 0 | 3.25 | 29.5001 | 3.5 | 1
General Cable Information
Cable ID |  | Number of Cores | Conductor Construction | Voltage [kV] | Conductor Area [mm²] | Cable Overall Diameter [in] | Maximum Steady-State Conductor Temperature [ºC] | Maximum Emergency Conductor Temperature [ºC]
HOMER CITY 345KV 5000KCMIL JULY |  | Single Core | 6 Segments | 345 | 2529.184 | 6.0332 | 90 | 110
Detailed Cable Information
Cable ID |  | Conductor | Insulation | Sheath / Tape | Concentric Wires | Filler | Armour | Jacket / Armour Serving
HOMER CITY 345KV 5000KCMIL JULY |  | Copper | XLPE Unfilled | Copper | Copper | n/a | n/a | Polyethylene
General Input Data
Cable | Cable ID | Circuit No. | Phase | Fq [Hz] | X [ft] | Y [ft] | DLF [p.u.] | Sheath / Shield Bonding
Cable Index Number | Cable Equipment ID | Circuit No. | Cable Phase | Operating Frequency | X coordinate | Y coordinate | Daily Load Factor | Bonding Type
1 | HOMER CITY 345KV 5000KCMIL JULY | 1 | A | 60 | -10.5 | 6.8279 | 1 | Multicables 1 Point Bonded
2 | HOMER CITY 345KV 5000KCMIL JULY | 1 | B | 60 | -11.5 | 5.8279 | 1 | Multicables 1 Point Bonded
3 | HOMER CITY 345KV 5000KCMIL JULY | 1 | C | 60 | -12.5 | 6.8279 | 1 | Multicables 1 Point Bonded
4 | HOMER CITY 345KV 5000KCMIL JULY | 1 | A | 60 | -10.5 | 5.8279 | 1 | Multicables 1 Point Bonded
5 | HOMER CITY 345KV 5000KCMIL JULY | 1 | B | 60 | -11.5 | 6.8279 | 1 | Multicables 1 Point Bonded
6 | HOMER CITY 345KV 5000KCMIL JULY | 1 | C | 60 | -12.5 | 5.8279 | 1 | Multicables 1 Point Bonded
7 | HOMER CITY 345KV 5000KCMIL JULY | 2 | A | 60 | -6 | 5.8279 | 1 | Multicables 1 Point Bonded
8 | HOMER CITY 345KV 5000KCMIL JULY | 2 | B | 60 | -7 | 6.8279 | 1 | Multicables 1 Point Bonded
9 | HOMER CITY 345KV 5000KCMIL JULY | 2 | C | 60 | -8 | 6.8279 | 1 | Multicables 1 Point Bonded
10 | HOMER CITY 345KV 5000KCMIL JULY | 2 | A | 60 | -6 | 6.8279 | 1 | Multicables 1 Point Bonded
11 | HOMER CITY 345KV 5000KCMIL JULY | 2 | B | 60 | -7 | 5.8279 | 1 | Multicables 1 Point Bonded
12 | HOMER CITY 345KV 5000KCMIL JULY | 2 | C | 60 | -8 | 5.8279 | 1 | Multicables 1 Point Bonded
13 | HOMER CITY 345KV 5000KCMIL JULY | 3 | A | 60 | -0.5 | 5.8279 | 1 | Multicables 1 Point Bonded
14 | HOMER CITY 345KV 5000KCMIL JULY | 3 | B | 60 | -1.5 | 6.8279 | 1 | Multicables 1 Point Bonded
15 | HOMER CITY 345KV 5000KCMIL JULY | 3 | C | 60 | -2.5 | 6.8279 | 1 | Multicables 1 Point Bonded
16 | HOMER CITY 345KV 5000KCMIL JULY | 3 | A | 60 | -0.5 | 6.8279 | 1 | Multicables 1 Point Bonded
17 | HOMER CITY 345KV 5000KCMIL JULY | 3 | B | 60 | -1.5 | 5.8279 | 1 | Multicables 1 Point Bonded
18 | HOMER CITY 345KV 5000KCMIL JULY | 3 | C | 60 | -2.5 | 5.8279 | 1 | Multicables 1 Point Bonded
19 | HOMER CITY 345KV 5000KCMIL JULY | 4 | A | 60 | 4 | 6.8279 | 1 | Multicables 1 Point Bonded
20 | HOMER CITY 345KV 5000KCMIL JULY | 4 | B | 60 | 3 | 5.8279 | 1 | Multicables 1 Point Bonded
21 | HOMER CITY 345KV 5000KCMIL JULY | 4 | C | 60 | 2 | 6.8279 | 1 | Multicables 1 Point Bonded
22 | HOMER CITY 345KV 5000KCMIL JULY | 4 | A | 60 | 4 | 5.8279 | 1 | Multicables 1 Point Bonded
23 | HOMER CITY 345KV 5000KCMIL JULY | 4 | B | 60 | 3 | 6.8279 | 1 | Multicables 1 Point Bonded
24 | HOMER CITY 345KV 5000KCMIL JULY | 4 | C | 60 | 2 | 5.8279 | 1 | Multicables 1 Point Bonded
25 | HOMER CITY 345KV 5000KCMIL JULY | 5 | A | 60 | 7.5 | 5.8279 | 1 | Multicables 1 Point Bonded
26 | HOMER CITY 345KV 5000KCMIL JULY | 5 | B | 60 | 6.5 | 5.8279 | 1 | Multicables 1 Point Bonded
27 | HOMER CITY 345KV 5000KCMIL JULY | 5 | C | 60 | 5.5 | 6.8279 | 1 | Multicables 1 Point Bonded
28 | HOMER CITY 345KV 5000KCMIL JULY | 5 | A | 60 | 7.5 | 6.8279 | 1 | Multicables 1 Point Bonded
29 | HOMER CITY 345KV 5000KCMIL JULY | 5 | B | 60 | 6.5 | 6.8279 | 1 | Multicables 1 Point Bonded
30 | HOMER CITY 345KV 5000KCMIL JULY | 5 | C | 60 | 5.5 | 5.8279 | 1 | Multicables 1 Point Bonded
31 | HOMER CITY 345KV 5000KCMIL JULY | 6 | A | 60 | 12 | 5.8279 | 1 | Multicables 1 Point Bonded
32 | HOMER CITY 345KV 5000KCMIL JULY | 6 | B | 60 | 11 | 5.8279 | 1 | Multicables 1 Point Bonded
33 | HOMER CITY 345KV 5000KCMIL JULY | 6 | C | 60 | 10 | 5.8279 | 1 | Multicables 1 Point Bonded
34 | HOMER CITY 345KV 5000KCMIL JULY | 6 | A | 60 | 12 | 6.8279 | 1 | Multicables 1 Point Bonded
35 | HOMER CITY 345KV 5000KCMIL JULY | 6 | B | 60 | 11 | 6.8279 | 1 | Multicables 1 Point Bonded
36 | HOMER CITY 345KV 5000KCMIL JULY | 6 | C | 60 | 10 | 6.8279 | 1 | Multicables 1 Point Bonded
Ampacity and Temperatures
Cable | Cable ID | I [A] | θc [°C] | θs [°C] | θa [°C] | θsurf [°C] | θduct [°C] | θair / θcasing [°C]
Cable Index Number | Cable Equipment ID | Steady State Ampacity | Conductor temperature | Sheath/Shield temperature | Armour temperature | Cable surface temperature | Duct surface temperature | Mean air temperature in the tunnel / Casing surface temperature
1 | HOMER CITY 345KV 5000KCMIL JULY | 384 | 69.7497 | 68.4058 | n/a | 68.0663 | 66.707 | n/a
2 | HOMER CITY 345KV 5000KCMIL JULY | 384 | 65.2792 | 63.9396 | n/a | 63.5776 | 62.1346 | n/a
3 | HOMER CITY 345KV 5000KCMIL JULY | 384 | 63.4671 | 62.1316 | n/a | 61.7913 | 60.3959 | n/a
4 | HOMER CITY 345KV 5000KCMIL JULY | 384 | 67.6543 | 66.3132 | n/a | 65.9739 | 64.6039 | n/a
5 | HOMER CITY 345KV 5000KCMIL JULY | 384 | 67.5649 | 66.2222 | n/a | 65.8589 | 64.4289 | n/a
6 | HOMER CITY 345KV 5000KCMIL JULY | 384 | 61.4043 | 60.0716 | n/a | 59.7315 | 58.3247 | n/a
7 | HOMER CITY 345KV 5000KCMIL JULY | 489 | 76.2106 | 74.4122 | n/a | 73.9923 | 72.3492 | n/a
8 | HOMER CITY 345KV 5000KCMIL JULY | 489 | 78.4733 | 76.6669 | n/a | 76.1962 | 74.4777 | n/a
9 | HOMER CITY 345KV 5000KCMIL JULY | 489 | 75.9406 | 74.1427 | n/a | 73.7233 | 72.0796 | n/a
10 | HOMER CITY 345KV 5000KCMIL JULY | 489 | 78.3929 | 76.5897 | n/a | 76.1692 | 74.5378 | n/a
11 | HOMER CITY 345KV 5000KCMIL JULY | 489 | 75.9948 | 74.1938 | n/a | 73.7276 | 71.9943 | n/a
12 | HOMER CITY 345KV 5000KCMIL JULY | 489 | 73.7119 | 71.9189 | n/a | 71.5001 | 69.8442 | n/a
13 | HOMER CITY 345KV 5000KCMIL JULY | 384 | 79.3995 | 78.0426 | n/a | 77.7036 | 76.3908 | n/a
14 | HOMER CITY 345KV 5000KCMIL JULY | 384 | 81.308 | 79.9468 | n/a | 79.581 | 78.2328 | n/a
15 | HOMER CITY 345KV 5000KCMIL JULY | 384 | 79.3915 | 78.0347 | n/a | 77.6951 | 76.3814 | n/a
16 | HOMER CITY 345KV 5000KCMIL JULY | 384 | 81.542 | 80.1823 | n/a | 79.8433 | 78.5398 | n/a
17 | HOMER CITY 345KV 5000KCMIL JULY | 384 | 79.0028 | 77.6448 | n/a | 77.2806 | 75.9215 | n/a
18 | HOMER CITY 345KV 5000KCMIL JULY | 384 | 77.365 | 76.0109 | n/a | 75.6715 | 74.3487 | n/a
19 | HOMER CITY 345KV 5000KCMIL JULY | 489 | 85.0243 | 83.2067 | n/a | 82.7854 | 81.1924 | n/a
20 | HOMER CITY 345KV 5000KCMIL JULY | 489 | 83.1238 | 81.3073 | n/a | 80.8398 | 79.1643 | n/a
21 | HOMER CITY 345KV 5000KCMIL JULY | 489 | 84.4446 | 82.6282 | n/a | 82.2065 | 80.6087 | n/a
22 | HOMER CITY 345KV 5000KCMIL JULY | 489 | 82.4468 | 80.6348 | n/a | 80.2146 | 78.6088 | n/a
23 | HOMER CITY 345KV 5000KCMIL JULY | 489 | 85.81 | 83.9877 | n/a | 83.5149 | 81.8538 | n/a
24 | HOMER CITY 345KV 5000KCMIL JULY | 489 | 82.0843 | 80.273 | n/a | 79.8522 | 78.2427 | n/a
25 | HOMER CITY 345KV 5000KCMIL JULY | 384 | 76.0546 | 74.7023 | n/a | 74.3631 | 73.0354 | n/a
26 | HOMER CITY 345KV 5000KCMIL JULY | 384 | 78.5083 | 77.1509 | n/a | 76.7929 | 75.4413 | n/a
27 | HOMER CITY 345KV 5000KCMIL JULY | 384 | 82.3629 | 81.0021 | n/a | 80.6629 | 79.3632 | n/a
28 | HOMER CITY 345KV 5000KCMIL JULY | 384 | 78.2098 | 76.8546 | n/a | 76.5153 | 75.1975 | n/a
29 | HOMER CITY 345KV 5000KCMIL JULY | 384 | 80.953 | 79.5924 | n/a | 79.2331 | 77.8929 | n/a
30 | HOMER CITY 345KV 5000KCMIL JULY | 384 | 79.9259 | 78.5684 | n/a | 78.2293 | 76.919 | n/a
31 | HOMER CITY 345KV 5000KCMIL JULY | 489 | 66.169 | 64.3924 | n/a | 63.974 | 62.269 | n/a
32 | HOMER CITY 345KV 5000KCMIL JULY | 489 | 70.4938 | 68.7049 | n/a | 68.2425 | 66.4675 | n/a
33 | HOMER CITY 345KV 5000KCMIL JULY | 489 | 72.6541 | 70.8634 | n/a | 70.4447 | 68.7827 | n/a
34 | HOMER CITY 345KV 5000KCMIL JULY | 489 | 68.3759 | 66.5945 | n/a | 66.1757 | 64.4842 | n/a
35 | HOMER CITY 345KV 5000KCMIL JULY | 489 | 73.0024 | 71.208 | n/a | 70.7417 | 68.983 | n/a
36 | HOMER CITY 345KV 5000KCMIL JULY | 489 | 74.9282 | 73.1326 | n/a | 72.7134 | 71.064 | n/a
Electrical Resistances
Cable | Cable ID | R₀ [Ω/mile] | ys | yp | R [Ω/mile] | R's [Ω/mile] | R'w [Ω/mile] | R'a [Ω/mile]
Cable Index Number | Cable Equipment ID | DC Resistance of the conductor at 20°C | Skin Effect Factor | Proximity Effect Factor | AC Resistance of Conductor at Operating Temperature | DC Resistance of Sheath at Operating Temperature | DC Resistance of Concentric Wires at Operating Temperature | DC Resistance of Armor at Operating Temperature
1 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.43786 | 0.012119 | 0.019398 | 0.6107 | 4.0506 | n/a
2 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.44686 | 0.01584 | 0.01928 | 0.60169 | 3.9909 | n/a
3 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.45059 | 0.012365 | 0.019167 | 0.59804 | 3.9667 | n/a
4 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.44204 | 0.0122 | 0.019321 | 0.60648 | 4.0226 | n/a
5 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.44222 | 0.015725 | 0.019364 | 0.60629 | 4.0214 | n/a
6 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.45489 | 0.012447 | 0.019091 | 0.59389 | 3.9391 | n/a
7 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.42531 | 0.01187 | 0.019635 | 0.62281 | 4.1309 | n/a
8 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.42104 | 0.015184 | 0.019765 | 0.62735 | 4.1611 | n/a
9 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.42582 | 0.011881 | 0.019625 | 0.62226 | 4.1273 | n/a
10 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.42119 | 0.011788 | 0.019715 | 0.6272 | 4.1601 | n/a
11 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.42572 | 0.015305 | 0.019674 | 0.62237 | 4.128 | n/a
12 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.4301 | 0.011966 | 0.019543 | 0.61778 | 4.0976 | n/a
13 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.41931 | 0.01175 | 0.019752 | 0.63013 | 4.1795 | n/a
14 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.41578 | 0.015047 | 0.019869 | 0.63397 | 4.205 | n/a
15 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.41932 | 0.01175 | 0.019751 | 0.63011 | 4.1794 | n/a
16 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.41535 | 0.011669 | 0.01983 | 0.63444 | 4.2081 | n/a
17 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.42005 | 0.015158 | 0.019784 | 0.62933 | 4.1742 | n/a
18 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.42312 | 0.011827 | 0.019677 | 0.62603 | 4.1523 | n/a
19 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.40902 | 0.01154 | 0.019958 | 0.64054 | 4.2486 | n/a
20 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.41245 | 0.014959 | 0.019935 | 0.63671 | 4.2232 | n/a
21 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.41006 | 0.011561 | 0.019937 | 0.63937 | 4.2408 | n/a
22 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.41369 | 0.011636 | 0.019864 | 0.63535 | 4.2142 | n/a
23 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.40761 | 0.014831 | 0.020034 | 0.64212 | 4.259 | n/a
24 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.41435 | 0.011649 | 0.01985 | 0.63462 | 4.2093 | n/a
25 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.42561 | 0.011876 | 0.019629 | 0.62339 | 4.1348 | n/a
26 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.42097 | 0.015182 | 0.019766 | 0.62833 | 4.1676 | n/a
27 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.41384 | 0.011639 | 0.019861 | 0.63609 | 4.2191 | n/a
28 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.42153 | 0.011795 | 0.019708 | 0.62773 | 4.1636 | n/a
29 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.41643 | 0.015064 | 0.019856 | 0.63325 | 4.2002 | n/a
30 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.41833 | 0.01173 | 0.019771 | 0.63119 | 4.1865 | n/a
31 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.44505 | 0.012258 | 0.019266 | 0.6026 | 3.9969 | n/a
32 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.43639 | 0.015578 | 0.019472 | 0.6113 | 4.0546 | n/a
33 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.43215 | 0.012006 | 0.019504 | 0.61565 | 4.0835 | n/a
34 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.4406 | 0.012172 | 0.019347 | 0.60704 | 4.0264 | n/a
35 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.43147 | 0.015453 | 0.019564 | 0.61635 | 4.0881 | n/a
36 | HOMER CITY 345KV 5000KCMIL JULY | 0.01119 | 0.42776 | 0.011919 | 0.019588 | 0.62023 | 4.1138 | n/a
Thermal Resistances
Cable | Cable ID | T₁ [K.m/W] | T₂ [K.m/W] | T₃ [K.m/W] | T₄' [K.m/W] | T₄'' [K.m/W] | T₄''' [K.m/W] | T₄ [K.m/W]
Cable Index Number | Cable Equipment ID | Thermal resistance of insulation | Thermal resistance of bedding | Thermal resistance of outer covering | Thermal resistance inside the duct | Thermal resistance of the duct | Thermal resistance of the external medium | Total external thermal resistance
1 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.19454 | 0.074104 | 9.3492 | 9.6178
2 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.19986 | 0.074104 | 8.1138 | 8.3877
3 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.20204 | 0.074104 | 8.1126 | 8.3888
4 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.19698 | 0.074104 | 8.9448 | 9.2159
5 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.19713 | 0.074104 | 8.5407 | 8.812
6 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.20463 | 0.074104 | 7.7122 | 7.9909
7 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.18808 | 0.074104 | 8.4487 | 8.7109
8 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.18574 | 0.074104 | 8.3281 | 8.588
9 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.18836 | 0.074104 | 8.4121 | 8.6746
10 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.18576 | 0.074104 | 8.7828 | 9.0427
11 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.18837 | 0.074104 | 7.9642 | 8.2266
12 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.19079 | 0.074104 | 8.0693 | 8.3342
13 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.18405 | 0.074104 | 11.2072 | 11.4653
14 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.18214 | 0.074104 | 11.1819 | 11.4382
15 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.18406 | 0.074104 | 11.1976 | 11.4558
16 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.18188 | 0.074104 | 11.6147 | 11.8706
17 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.18449 | 0.074104 | 10.7547 | 11.0133
18 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.18617 | 0.074104 | 10.8114 | 11.0716
19 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.17907 | 0.074104 | 9.8202 | 10.0733
20 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.18099 | 0.074104 | 9.0987 | 9.3538
21 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.17964 | 0.074104 | 9.7203 | 9.974
22 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.18161 | 0.074104 | 9.4289 | 9.6847
23 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.17835 | 0.074104 | 9.492 | 9.7445
24 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.18198 | 0.074104 | 9.362 | 9.6181
25 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.18756 | 0.074104 | 10.5704 | 10.8321
26 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.185 | 0.074104 | 10.7433 | 11.0024
27 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.18106 | 0.074104 | 11.772 | 12.0272
28 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.18528 | 0.074104 | 10.9821 | 11.2415
29 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.18249 | 0.074104 | 11.1993 | 11.4559
30 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.18351 | 0.074104 | 11.3089 | 11.5665
31 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.19951 | 0.074104 | 6.8794 | 7.153
32 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.19449 | 0.074104 | 7.1221 | 7.3907
33 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.19197 | 0.074104 | 7.9055 | 8.1715
34 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.19688 | 0.074104 | 7.2224 | 7.4934
35 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.19165 | 0.074104 | 7.4922 | 7.7579
36 | HOMER CITY 345KV 5000KCMIL JULY | 0.39868 | 0 | 0.067863 | 0.18946 | 0.074104 | 8.2558 | 8.5194
Losses
Cable | Cable ID | Wc [W/ft] | Wd [W/ft] | Ws [W/ft] | Wa [W/ft] | Wt [W/ft] | ƛ₁ | ƛ₂
Cable Index Number | Cable Equipment ID | Conductor Losses | Dielectric Losses | Metallic Screen Losses | Armor/Pipe Losses | Total Losses | Screen Loss Factor | Armour Loss Factor + Pipe Loss Factor
1 | HOMER CITY 345KV 5000KCMIL JULY | 0.54172 | 0.97151 | 0.02906 | 0 | 1.5423 | 0.053643 | 0
2 | HOMER CITY 345KV 5000KCMIL JULY | 0.53844 | 0.97151 | 0.095402 | 0 | 1.6054 | 0.17718 | 0
3 | HOMER CITY 345KV 5000KCMIL JULY | 0.53528 | 0.97151 | 0.033461 | 0 | 1.5403 | 0.06251 | 0
4 | HOMER CITY 345KV 5000KCMIL JULY | 0.53957 | 0.97151 | 0.02926 | 0 | 1.5403 | 0.054229 | 0
5 | HOMER CITY 345KV 5000KCMIL JULY | 0.54079 | 0.97151 | 0.09468 | 0 | 1.607 | 0.17508 | 0
6 | HOMER CITY 345KV 5000KCMIL JULY | 0.53317 | 0.97151 | 0.033694 | 0 | 1.5384 | 0.063195 | 0
7 | HOMER CITY 345KV 5000KCMIL JULY | 0.88922 | 0.97151 | 0.049498 | 0 | 1.9102 | 0.055664 | 0
8 | HOMER CITY 345KV 5000KCMIL JULY | 0.8951 | 0.97151 | 0.14917 | 0 | 2.0158 | 0.16665 | 0
9 | HOMER CITY 345KV 5000KCMIL JULY | 0.88877 | 0.97151 | 0.048481 | 0 | 1.9088 | 0.054549 | 0
10 | HOMER CITY 345KV 5000KCMIL JULY | 0.89285 | 0.97151 | 0.049153 | 0 | 1.9135 | 0.055052 | 0
11 | HOMER CITY 345KV 5000KCMIL JULY | 0.89098 | 0.97151 | 0.15036 | 0 | 2.0129 | 0.16876 | 0
12 | HOMER CITY 345KV 5000KCMIL JULY | 0.88507 | 0.97151 | 0.048832 | 0 | 1.9054 | 0.055173 | 0
13 | HOMER CITY 345KV 5000KCMIL JULY | 0.55161 | 0.97151 | 0.026847 | 0 | 1.55 | 0.04867 | 0
14 | HOMER CITY 345KV 5000KCMIL JULY | 0.55488 | 0.97151 | 0.07729 | 0 | 1.6037 | 0.13929 | 0
15 | HOMER CITY 345KV 5000KCMIL JULY | 0.55161 | 0.97151 | 0.027922 | 0 | 1.551 | 0.050619 | 0
16 | HOMER CITY 345KV 5000KCMIL JULY | 0.55381 | 0.97151 | 0.026665 | 0 | 1.552 | 0.048148 | 0
17 | HOMER CITY 345KV 5000KCMIL JULY | 0.55251 | 0.97151 | 0.077857 | 0 | 1.6019 | 0.14091 | 0
18 | HOMER CITY 345KV 5000KCMIL JULY | 0.54953 | 0.97151 | 0.028102 | 0 | 1.5491 | 0.051139 | 0
19 | HOMER CITY 345KV 5000KCMIL JULY | 0.90387 | 0.97151 | 0.04254 | 0 | 1.9179 | 0.047065 | 0
20 | HOMER CITY 345KV 5000KCMIL JULY | 0.90283 | 0.97151 | 0.12773 | 0 | 2.0021 | 0.14147 | 0
21 | HOMER CITY 345KV 5000KCMIL JULY | 0.90291 | 0.97151 | 0.044909 | 0 | 1.9193 | 0.049739 | 0
22 | HOMER CITY 345KV 5000KCMIL JULY | 0.89959 | 0.97151 | 0.042885 | 0 | 1.914 | 0.047672 | 0
23 | HOMER CITY 345KV 5000KCMIL JULY | 0.9073 | 0.97151 | 0.12665 | 0 | 2.0055 | 0.13959 | 0
24 | HOMER CITY 345KV 5000KCMIL JULY | 0.89898 | 0.97151 | 0.045243 | 0 | 1.9157 | 0.050327 | 0
25 | HOMER CITY 345KV 5000KCMIL JULY | 0.54818 | 0.97151 | 0.02689 | 0 | 1.5466 | 0.049053 | 0
26 | HOMER CITY 345KV 5000KCMIL JULY | 0.55201 | 0.97151 | 0.066436 | 0 | 1.59 | 0.12035 | 0
27 | HOMER CITY 345KV 5000KCMIL JULY | 0.55465 | 0.97151 | 0.026393 | 0 | 1.5526 | 0.047585 | 0
28 | HOMER CITY 345KV 5000KCMIL JULY | 0.55039 | 0.97151 | 0.026705 | 0 | 1.5486 | 0.048519 | 0
29 | HOMER CITY 345KV 5000KCMIL JULY | 0.55451 | 0.97151 | 0.065922 | 0 | 1.5919 | 0.11888 | 0
30 | HOMER CITY 345KV 5000KCMIL JULY | 0.55215 | 0.97151 | 0.026597 | 0 | 1.5503 | 0.04817 | 0
31 | HOMER CITY 345KV 5000KCMIL JULY | 0.87253 | 0.97151 | 0.055328 | 0 | 1.8994 | 0.063411 | 0
32 | HOMER CITY 345KV 5000KCMIL JULY | 0.88183 | 0.97151 | 0.16096 | 0 | 2.0143 | 0.18253 | 0
33 | HOMER CITY 345KV 5000KCMIL JULY | 0.88331 | 0.97151 | 0.049159 | 0 | 1.904 | 0.055654 | 0
34 | HOMER CITY 345KV 5000KCMIL JULY | 0.8762 | 0.97151 | 0.054926 | 0 | 1.9026 | 0.062687 | 0
35 | HOMER CITY 345KV 5000KCMIL JULY | 0.886 | 0.97151 | 0.15965 | 0 | 2.0172 | 0.18019 | 0
36 | HOMER CITY 345KV 5000KCMIL JULY | 0.88709 | 0.97151 | 0.048798 | 0 | 1.9074 | 0.055009 | 0
Complementary Information
Cable | Cable ID | Δθint [°C] | [A] | [µF/mile] | [Ω] | [Ω/mile] | [Ω/mile] | [V/A/mile]
Cable Index Number | Cable Equipment ID | Temperature rise due to surrounding heat sources | Induced current on Metallic Screen | Cable Capacitance | Surge Impedance | Reactance of Conductor | Reactance of Metallic Sheath | Voltage drop for Three Phase System
1 | HOMER CITY 345KV 5000KCMIL JULY | 43.792 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.033598
2 | HOMER CITY 345KV 5000KCMIL JULY | 39.279 | 0 | 0.34279 | 50.1227 | 0.32481 | 0 | 0.033394
3 | HOMER CITY 345KV 5000KCMIL JULY | 37.4615 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.033198
4 | HOMER CITY 345KV 5000KCMIL JULY | 41.9309 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.033464
5 | HOMER CITY 345KV 5000KCMIL JULY | 41.3003 | 0 | 0.34279 | 50.1227 | 0.32481 | 0 | 0.03354
6 | HOMER CITY 345KV 5000KCMIL JULY | 35.6535 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.033067
7 | HOMER CITY 345KV 5000KCMIL JULY | 48.8612 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.034008
8 | HOMER CITY 345KV 5000KCMIL JULY | 50.3812 | 0 | 0.34279 | 50.1227 | 0.32481 | 0 | 0.034233
9 | HOMER CITY 345KV 5000KCMIL JULY | 48.3149 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.033991
10 | HOMER CITY 345KV 5000KCMIL JULY | 50.7638 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.034147
11 | HOMER CITY 345KV 5000KCMIL JULY | 48.2169 | 0 | 0.34279 | 50.1227 | 0.32481 | 0 | 0.034076
12 | HOMER CITY 345KV 5000KCMIL JULY | 46.3696 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.033849
13 | HOMER CITY 345KV 5000KCMIL JULY | 53.64 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.034211
14 | HOMER CITY 345KV 5000KCMIL JULY | 55.0711 | 0 | 0.34279 | 50.1227 | 0.32481 | 0 | 0.034413
15 | HOMER CITY 345KV 5000KCMIL JULY | 53.4216 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.034211
16 | HOMER CITY 345KV 5000KCMIL JULY | 55.5547 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.034347
17 | HOMER CITY 345KV 5000KCMIL JULY | 53.0126 | 0 | 0.34279 | 50.1227 | 0.32481 | 0 | 0.034267
18 | HOMER CITY 345KV 5000KCMIL JULY | 51.6191 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.034082
19 | HOMER CITY 345KV 5000KCMIL JULY | 57.299 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.034569
20 | HOMER CITY 345KV 5000KCMIL JULY | 55.3494 | 0 | 0.34279 | 50.1227 | 0.32481 | 0 | 0.034529
21 | HOMER CITY 345KV 5000KCMIL JULY | 56.7622 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.034532
22 | HOMER CITY 345KV 5000KCMIL JULY | 55.0243 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.034405
23 | HOMER CITY 345KV 5000KCMIL JULY | 57.7129 | 0 | 0.34279 | 50.1227 | 0.32481 | 0 | 0.0347
24 | HOMER CITY 345KV 5000KCMIL JULY | 54.6901 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.034382
25 | HOMER CITY 345KV 5000KCMIL JULY | 50.309 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.033998
26 | HOMER CITY 345KV 5000KCMIL JULY | 52.5515 | 0 | 0.34279 | 50.1227 | 0.32481 | 0 | 0.034235
27 | HOMER CITY 345KV 5000KCMIL JULY | 56.3316 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.0344
28 | HOMER CITY 345KV 5000KCMIL JULY | 52.2349 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.034135
29 | HOMER CITY 345KV 5000KCMIL JULY | 54.746 | 0 | 0.34279 | 50.1227 | 0.32481 | 0 | 0.034391
30 | HOMER CITY 345KV 5000KCMIL JULY | 54.136 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.034245
31 | HOMER CITY 345KV 5000KCMIL JULY | 38.8514 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.03337
32 | HOMER CITY 345KV 5000KCMIL JULY | 42.7287 | 0 | 0.34279 | 50.1227 | 0.32481 | 0 | 0.033726
33 | HOMER CITY 345KV 5000KCMIL JULY | 45.3262 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.033782
34 | HOMER CITY 345KV 5000KCMIL JULY | 40.7531 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.03351
35 | HOMER CITY 345KV 5000KCMIL JULY | 44.9082 | 0 | 0.34279 | 50.1227 | 0.32481 | 0 | 0.033885
36 | HOMER CITY 345KV 5000KCMIL JULY | 47.3104 | 0 | 0.34279 | 51.2916 | 0.34014 | 0 | 0.033927

## Study Summary
Study Summary
CYMCAP Version |  | 8.2 Revision 3
Study: |  | HOMER CITY GENERATION
Execution: |  | Three Units Deepest Depth 12 31
Date: |  | 1/8/2026 12:32:16 PM
General Simulation Data
Steady State Option | [8 empty] | Temperature
Consider Electrical interaction between circuits | [8 empty] | No
Induced currents in metallic layers as a fraction of conductor current (applied to all single phase circuits) : | [8 empty] | 0
Conductor Resistances Computation Option: | [8 empty] | IEC-228
Standard Settings Options
General guidance | [8 empty] | Custom
Factor on RAC due to magnetic armour | [8 empty] | CIGREGuidance
Factor on RAC due to magnetic duct | [8 empty] | CIGREGuidance
Factor on ƛ₁ due to magnetic armour | [8 empty] | CYMCAPGuidance
Factor on ƛ₁ due to magnetic duct | [8 empty] | CIGREGuidance
Factor on ƛ₂ due to ƛ'₁ | [8 empty] | CYMCAPGuidance
ƛ''₁ computation | [8 empty] | CIGREGuidance
ƛ₂pipe computation | [8 empty] | CYMCAPGuidance
Wd computation | [8 empty] | CIGREGuidance
T₂ computation | [8 empty] | CIGREGuidance
T₄ computation | [8 empty] | CYMCAPGuidance
Installation Type:Multiple Ductbanks/Backfills
Ambient Soil Temperature at Installation Depth [°C] | [8 empty] | 19.4
Native Soil Thermal Resistivity [K.m/W] | [8 empty] | 1.3
Consider Non-Isothermal Earth Surface | [8 empty] | No
Layer Name |  | X [ft] | Y [ft] | Width [ft] | Height [ft] | Thermal Resistivity [K.m/W]
Unit 3000 |  | 4.5112e-05 | 6.25 | 27.5001 | 2.5 | 0.6
Surface Ag |  | 0 | 0.75 | 29.5001 | 1.5 | 5
Gravel Bed |  | 0 | 7.75 | 27.5001 | 0.5 | 5
Backfill |  | 0 | 3.25 | 29.5001 | 3.5 | 1
Results Summary
Cable No. | Cable ID | Circuit No. | Feeder ID | Cable Phase | Cable Frequency | Daily Load Factor | X coordinate [ft] | Y coordinate [ft] | Conductor temperature [°C] | Ampacity [A]
1 | HOMER CITY 345KV 5000KCMIL JULY | 1 |  | A | 60 | 1 | -10.5 | 6.8279 | 69.7497 | 384
2 | HOMER CITY 345KV 5000KCMIL JULY | 1 |  | B | 60 | 1 | -11.5 | 5.8279 | 65.2792 | 384
3 | HOMER CITY 345KV 5000KCMIL JULY | 1 |  | C | 60 | 1 | -12.5 | 6.8279 | 63.4671 | 384
4 | HOMER CITY 345KV 5000KCMIL JULY | 1 |  | A | 60 | 1 | -10.5 | 5.8279 | 67.6543 | 384
5 | HOMER CITY 345KV 5000KCMIL JULY | 1 |  | B | 60 | 1 | -11.5 | 6.8279 | 67.5649 | 384
6 | HOMER CITY 345KV 5000KCMIL JULY | 1 |  | C | 60 | 1 | -12.5 | 5.8279 | 61.4043 | 384
7 | HOMER CITY 345KV 5000KCMIL JULY | 2 |  | A | 60 | 1 | -6 | 5.8279 | 76.2106 | 489
8 | HOMER CITY 345KV 5000KCMIL JULY | 2 |  | B | 60 | 1 | -7 | 6.8279 | 78.4733 | 489
9 | HOMER CITY 345KV 5000KCMIL JULY | 2 |  | C | 60 | 1 | -8 | 6.8279 | 75.9406 | 489
10 | HOMER CITY 345KV 5000KCMIL JULY | 2 |  | A | 60 | 1 | -6 | 6.8279 | 78.3929 | 489
11 | HOMER CITY 345KV 5000KCMIL JULY | 2 |  | B | 60 | 1 | -7 | 5.8279 | 75.9948 | 489
12 | HOMER CITY 345KV 5000KCMIL JULY | 2 |  | C | 60 | 1 | -8 | 5.8279 | 73.7119 | 489
13 | HOMER CITY 345KV 5000KCMIL JULY | 3 |  | A | 60 | 1 | -0.5 | 5.8279 | 79.3995 | 384
14 | HOMER CITY 345KV 5000KCMIL JULY | 3 |  | B | 60 | 1 | -1.5 | 6.8279 | 81.308 | 384
15 | HOMER CITY 345KV 5000KCMIL JULY | 3 |  | C | 60 | 1 | -2.5 | 6.8279 | 79.3915 | 384
16 | HOMER CITY 345KV 5000KCMIL JULY | 3 |  | A | 60 | 1 | -0.5 | 6.8279 | 81.542 | 384
17 | HOMER CITY 345KV 5000KCMIL JULY | 3 |  | B | 60 | 1 | -1.5 | 5.8279 | 79.0028 | 384
18 | HOMER CITY 345KV 5000KCMIL JULY | 3 |  | C | 60 | 1 | -2.5 | 5.8279 | 77.365 | 384
19 | HOMER CITY 345KV 5000KCMIL JULY | 4 |  | A | 60 | 1 | 4 | 6.8279 | 85.0243 | 489
20 | HOMER CITY 345KV 5000KCMIL JULY | 4 |  | B | 60 | 1 | 3 | 5.8279 | 83.1238 | 489
21 | HOMER CITY 345KV 5000KCMIL JULY | 4 |  | C | 60 | 1 | 2 | 6.8279 | 84.4446 | 489
22 | HOMER CITY 345KV 5000KCMIL JULY | 4 |  | A | 60 | 1 | 4 | 5.8279 | 82.4468 | 489
23 | HOMER CITY 345KV 5000KCMIL JULY | 4 |  | B | 60 | 1 | 3 | 6.8279 | 85.81 | 489
24 | HOMER CITY 345KV 5000KCMIL JULY | 4 |  | C | 60 | 1 | 2 | 5.8279 | 82.0843 | 489
25 | HOMER CITY 345KV 5000KCMIL JULY | 5 |  | A | 60 | 1 | 7.5 | 5.8279 | 76.0546 | 384
26 | HOMER CITY 345KV 5000KCMIL JULY | 5 |  | B | 60 | 1 | 6.5 | 5.8279 | 78.5083 | 384
27 | HOMER CITY 345KV 5000KCMIL JULY | 5 |  | C | 60 | 1 | 5.5 | 6.8279 | 82.3629 | 384
28 | HOMER CITY 345KV 5000KCMIL JULY | 5 |  | A | 60 | 1 | 7.5 | 6.8279 | 78.2098 | 384
29 | HOMER CITY 345KV 5000KCMIL JULY | 5 |  | B | 60 | 1 | 6.5 | 6.8279 | 80.953 | 384
30 | HOMER CITY 345KV 5000KCMIL JULY | 5 |  | C | 60 | 1 | 5.5 | 5.8279 | 79.9259 | 384
31 | HOMER CITY 345KV 5000KCMIL JULY | 6 |  | A | 60 | 1 | 12 | 5.8279 | 66.169 | 489
32 | HOMER CITY 345KV 5000KCMIL JULY | 6 |  | B | 60 | 1 | 11 | 5.8279 | 70.4938 | 489
33 | HOMER CITY 345KV 5000KCMIL JULY | 6 |  | C | 60 | 1 | 10 | 5.8279 | 72.6541 | 489
34 | HOMER CITY 345KV 5000KCMIL JULY | 6 |  | A | 60 | 1 | 12 | 6.8279 | 68.3759 | 489
35 | HOMER CITY 345KV 5000KCMIL JULY | 6 |  | B | 60 | 1 | 11 | 6.8279 | 73.0024 | 489
36 | HOMER CITY 345KV 5000KCMIL JULY | 6 |  | C | 60 | 1 | 10 | 6.8279 | 74.9282 | 489

## Steady State Summary
Steady State Summary
CYMCAP Version |  | 8.2 Revision 3
Study: |  | HOMER CITY GENERATION
Execution: |  | Three Units Deepest Depth 12 31
Date: |  | 1/8/2026 12:32:16 PM
Simulation Data
Installation type: |  | Multiple Ductbanks
Steady State Option |  | Temperature
Ambient temperature [°C] |  | 19.4
Native Soil Thermal Resistivity [K.m/W] |  | 1.3
Consider Non-Isothermal Earth Surface |  | No
Consider effect of soil dry out |  | No
Consider Electrical interaction between circuits |  | No
Induced current in metallic layers as a fraction of conductor current (applied to all single phase circuits) [A] |  | 0
Variable | Description |  | Unit | Cables
Cable No. | Cable Index Number |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36
General Input Data
Cable ID | Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY
Circuit No. | Circuit No. |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
Phase | Cable Phase |  |  | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C
Fq | Operating Frequency |  | [Hz] | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
x | X coordinate |  | [ft] | -10.5 | -11.5 | -12.5 | -10.5 | -11.5 | -12.5 | -6 | -7 | -8 | -6 | -7 | -8 | -0.5 | -1.5 | -2.5 | -0.5 | -1.5 | -2.5 | 4 | 3 | 2 | 4 | 3 | 2 | 7.5 | 6.5 | 5.5 | 7.5 | 6.5 | 5.5 | 12 | 11 | 10 | 12 | 11 | 10
y | Y coordinate |  | [ft] | 6.8279 | 5.8279 | 6.8279 | 5.8279 | 6.8279 | 5.8279 | 5.8279 | 6.8279 | 6.8279 | 6.8279 | 5.8279 | 5.8279 | 5.8279 | 6.8279 | 6.8279 | 6.8279 | 5.8279 | 5.8279 | 6.8279 | 5.8279 | 6.8279 | 5.8279 | 6.8279 | 5.8279 | 5.8279 | 5.8279 | 6.8279 | 6.8279 | 6.8279 | 5.8279 | 5.8279 | 5.8279 | 5.8279 | 6.8279 | 6.8279 | 6.8279
DLF | Daily Load Factor |  | [p.u.] | bar: Cables 1 to Cables 36
| Bonding Type |  |  | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded | Multicables 1 Point Bonded
Ampacity
I | Steady State Ampacity |  | [A] | 384 | 384 | 384 | 384 | 384 | 384 | 489 | 489 | 489 | 489 | 489 | 489 | 384 | 384 | 384 | 384 | 384 | 384 | 489 | 489 | 489 | 489 | 489 | 489 | 384 | 384 | 384 | 384 | 384 | 384 | 489 | 489 | 489 | 489 | 489 | 489
I₀ | Steady State Ampacity without insulation temperature drop constraint |  | [A] | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Temperatures
θc | Conductor temperature |  | [°C] | 69.7497 | 65.2792 | 63.4671 | 67.6543 | 67.5649 | 61.4043 | 76.2106 | 78.4733 | 75.9406 | 78.3929 | 75.9948 | 73.7119 | 79.3995 | 81.308 | 79.3915 | 81.542 | 79.0028 | 77.365 | 85.0243 | 83.1238 | 84.4446 | 82.4468 | 85.81 | 82.0843 | 76.0546 | 78.5083 | 82.3629 | 78.2098 | 80.953 | 79.9259 | 66.169 | 70.4938 | 72.6541 | 68.3759 | 73.0024 | 74.9282
Δθins | Temperature drop across the insulation |  | [°C] | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
θs | Sheath/Shield temperature |  | [°C] | 68.4058 | 63.9396 | 62.1316 | 66.3132 | 66.2222 | 60.0716 | 74.4122 | 76.6669 | 74.1427 | 76.5897 | 74.1938 | 71.9189 | 78.0426 | 79.9468 | 78.0347 | 80.1823 | 77.6448 | 76.0109 | 83.2067 | 81.3073 | 82.6282 | 80.6348 | 83.9877 | 80.273 | 74.7023 | 77.1509 | 81.0021 | 76.8546 | 79.5924 | 78.5684 | 64.3924 | 68.7049 | 70.8634 | 66.5945 | 71.208 | 73.1326
θa | Armour temperature |  | [°C] | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
θsurf | Cable surface temperature |  | [°C] | 68.0663 | 63.5776 | 61.7913 | 65.9739 | 65.8589 | 59.7315 | 73.9923 | 76.1962 | 73.7233 | 76.1692 | 73.7276 | 71.5001 | 77.7036 | 79.581 | 77.6951 | 79.8433 | 77.2806 | 75.6715 | 82.7854 | 80.8398 | 82.2065 | 80.2146 | 83.5149 | 79.8522 | 74.3631 | 76.7929 | 80.6629 | 76.5153 | 79.2331 | 78.2293 | 63.974 | 68.2425 | 70.4447 | 66.1757 | 70.7417 | 72.7134
θduct | Duct surface temperature |  | [°C] | 66.707 | 62.1346 | 60.3959 | 64.6039 | 64.4289 | 58.3247 | 72.3492 | 74.4777 | 72.0796 | 74.5378 | 71.9943 | 69.8442 | 76.3908 | 78.2328 | 76.3814 | 78.5398 | 75.9215 | 74.3487 | 81.1924 | 79.1643 | 80.6087 | 78.6088 | 81.8538 | 78.2427 | 73.0354 | 75.4413 | 79.3632 | 75.1975 | 77.8929 | 76.919 | 62.269 | 66.4675 | 68.7827 | 64.4842 | 68.983 | 71.064
Resistances
R₀ | DC Resistance of the conductor at 20°C |  | [Ω/mile] | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119
R | AC Resistance of the Conductor at Operating Temperature |  | [Ω/mile] | 0.019398 | 0.01928 | 0.019167 | 0.019321 | 0.019364 | 0.019091 | 0.019635 | 0.019765 | 0.019625 | 0.019715 | 0.019674 | 0.019543 | 0.019752 | 0.019869 | 0.019751 | 0.01983 | 0.019784 | 0.019677 | 0.019958 | 0.019935 | 0.019937 | 0.019864 | 0.020034 | 0.01985 | 0.019629 | 0.019766 | 0.019861 | 0.019708 | 0.019856 | 0.019771 | 0.019266 | 0.019472 | 0.019504 | 0.019347 | 0.019564 | 0.019588
ys | Skin Effect Factor |  |  | 0.43786 | 0.44686 | 0.45059 | 0.44204 | 0.44222 | 0.45489 | 0.42531 | 0.42104 | 0.42582 | 0.42119 | 0.42572 | 0.4301 | 0.41931 | 0.41578 | 0.41932 | 0.41535 | 0.42005 | 0.42312 | 0.40902 | 0.41245 | 0.41006 | 0.41369 | 0.40761 | 0.41435 | 0.42561 | 0.42097 | 0.41384 | 0.42153 | 0.41643 | 0.41833 | 0.44505 | 0.43639 | 0.43215 | 0.4406 | 0.43147 | 0.42776
yp | Proximity Effect Factor |  |  | 0.012119 | 0.01584 | 0.012365 | 0.0122 | 0.015725 | 0.012447 | 0.01187 | 0.015184 | 0.011881 | 0.011788 | 0.015305 | 0.011966 | 0.01175 | 0.015047 | 0.01175 | 0.011669 | 0.015158 | 0.011827 | 0.01154 | 0.014959 | 0.011561 | 0.011636 | 0.014831 | 0.011649 | 0.011876 | 0.015182 | 0.011639 | 0.011795 | 0.015064 | 0.01173 | 0.012258 | 0.015578 | 0.012006 | 0.012172 | 0.015453 | 0.011919
Losses
Wc | Conductor Losses |  | [W/ft] | 0.54172 | 0.53844 | 0.53528 | 0.53957 | 0.54079 | 0.53317 | 0.88922 | 0.8951 | 0.88877 | 0.89285 | 0.89098 | 0.88507 | 0.55161 | 0.55488 | 0.55161 | 0.55381 | 0.55251 | 0.54953 | 0.90387 | 0.90283 | 0.90291 | 0.89959 | 0.9073 | 0.89898 | 0.54818 | 0.55201 | 0.55465 | 0.55039 | 0.55451 | 0.55215 | 0.87253 | 0.88183 | 0.88331 | 0.8762 | 0.886 | 0.88709
Wd | Dielectric Losses |  | [W/ft] | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151
Ws | Metallic Screen Losses |  | [W/ft] | 0.02906 | 0.095402 | 0.033461 | 0.02926 | 0.09468 | 0.033694 | 0.049498 | 0.14917 | 0.048481 | 0.049153 | 0.15036 | 0.048832 | 0.026847 | 0.07729 | 0.027922 | 0.026665 | 0.077857 | 0.028102 | 0.04254 | 0.12773 | 0.044909 | 0.042885 | 0.12665 | 0.045243 | 0.02689 | 0.066436 | 0.026393 | 0.026705 | 0.065922 | 0.026597 | 0.055328 | 0.16096 | 0.049159 | 0.054926 | 0.15965 | 0.048798
Wa | Armor/Pipe Losses |  | [W/ft] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wt | Total Losses |  | [W/ft] | 1.5423 | 1.6054 | 1.5403 | 1.5403 | 1.607 | 1.5384 | 1.9102 | 2.0158 | 1.9088 | 1.9135 | 2.0129 | 1.9054 | 1.55 | 1.6037 | 1.551 | 1.552 | 1.6019 | 1.5491 | 1.9179 | 2.0021 | 1.9193 | 1.914 | 2.0055 | 1.9157 | 1.5466 | 1.59 | 1.5526 | 1.5486 | 1.5919 | 1.5503 | 1.8994 | 2.0143 | 1.904 | 1.9026 | 2.0172 | 1.9074
ƛ₁ | Screen Loss Factor |  |  | 0.053643 | 0.17718 | 0.06251 | 0.054229 | 0.17508 | 0.063195 | 0.055664 | 0.16665 | 0.054549 | 0.055052 | 0.16876 | 0.055173 | 0.04867 | 0.13929 | 0.050619 | 0.048148 | 0.14091 | 0.051139 | 0.047065 | 0.14147 | 0.049739 | 0.047672 | 0.13959 | 0.050327 | 0.049053 | 0.12035 | 0.047585 | 0.048519 | 0.11888 | 0.04817 | 0.063411 | 0.18253 | 0.055654 | 0.062687 | 0.18019 | 0.055009
ƛ₂ | Armour Loss Factor + Pipe Loss Factor |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Thermal resistances
T1 | Thermal Resistance Between Conductor and Screen |  | [K.m/W] | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868
T2 | Thermal Resistance Between Screen and Armour |  | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
T3 | Thermal Resistance of the Jacket/Pipe Coating |  | [K.m/W] | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863
T4 | Total external thermal resistance |  | [K.m/W] | 9.6178 | 8.3877 | 8.3888 | 9.2159 | 8.812 | 7.9909 | 8.7109 | 8.588 | 8.6746 | 9.0427 | 8.2266 | 8.3342 | 11.4653 | 11.4382 | 11.4558 | 11.8706 | 11.0133 | 11.0716 | 10.0733 | 9.3538 | 9.974 | 9.6847 | 9.7445 | 9.6181 | 10.8321 | 11.0024 | 12.0272 | 11.2415 | 11.4559 | 11.5665 | 7.153 | 7.3907 | 8.1715 | 7.4934 | 7.7579 | 8.5194
Others
Δθint | Temperature rise due to surrounding heat sources |  | [°C] | 43.792 | 39.279 | 37.4615 | 41.9309 | 41.3003 | 35.6535 | 48.8612 | 50.3812 | 48.3149 | 50.7638 | 48.2169 | 46.3696 | 53.64 | 55.0711 | 53.4216 | 55.5547 | 53.0126 | 51.6191 | 57.299 | 55.3494 | 56.7622 | 55.0243 | 57.7129 | 54.6901 | 50.309 | 52.5515 | 56.3316 | 52.2349 | 54.746 | 54.136 | 38.8514 | 42.7287 | 45.3262 | 40.7531 | 44.9082 | 47.3104
| Induced Voltage (standing) on Sheath |  | [V/mile] | 24.5826 | 124.7403 | 204.2962 | 24.5927 | 124.7517 | 204.3023 | 103.3151 | 111.5703 | 176.0972 | 103.3177 | 111.5642 | 176.1047 | 72.6345 | 84.9115 | 130.1541 | 72.6353 | 84.9071 | 130.1591 | 124.4594 | 102.4351 | 135.3733 | 124.4558 | 102.4343 | 135.3799 | 151.1044 | 96.344 | 40.6889 | 151.1079 | 96.3327 | 40.6856 | 236.9844 | 140.8768 | 52.8351 | 236.99 | 140.8607 | 52.8351
| Induced Voltage angle on Sheath |  | [°] | -63.0803 | 138.6466 | -174.6498 | -63.1075 | 138.652 | -174.6538 | -14.3733 | 109.6488 | -171.4452 | -14.3618 | 109.6376 | -171.4516 | -19.1966 | 109.6542 | -170.0748 | -19.1841 | 109.6435 | -170.081 | -14.1672 | 92.1454 | -168.0028 | -14.1782 | 92.159 | -168.0117 | -9.3384 | 53.8249 | -136.9313 | -9.3325 | 53.8327 | -136.9555 | -5.6809 | 48.867 | -150.4336 | -5.676 | 48.8735 | -150.4105
| Induced Voltage (standing) on Concentric Wires |  | [V/mile] | 25.2925 | 125.2983 | 205.062 | 25.3025 | 125.3098 | 205.0682 | 104.3485 | 112.5811 | 177.096 | 104.351 | 112.575 | 177.1035 | 73.462 | 85.7053 | 130.9455 | 73.4629 | 85.7008 | 130.9505 | 125.4918 | 103.507 | 136.3938 | 125.4881 | 103.5062 | 136.4005 | 151.8928 | 97.0253 | 41.5099 | 151.8963 | 97.0139 | 41.5066 | 237.9622 | 141.6866 | 53.9077 | 237.9679 | 141.6703 | 53.9077
| Induced Voltage angle on Concentric Wires |  | [°] | -62.0385 | 138.3574 | -174.5517 | -62.0659 | 138.3629 | -174.5556 | -14.532 | 109.4653 | -171.3183 | -14.5205 | 109.4541 | -171.3247 | -19.3198 | 109.4649 | -169.9482 | -19.3072 | 109.4541 | -169.9545 | -14.3008 | 92.1231 | -167.8635 | -14.3118 | 92.1367 | -167.8724 | -9.4506 | 54.1184 | -137.194 | -9.4446 | 54.1263 | -137.2181 | -5.7873 | 49.1523 | -150.4251 | -5.7823 | 49.1589 | -150.4022
| Induced current on Metallic Screen |  | [A] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Cable - HO...5KV 5000KCMIL JULY
Cables Report
CYMCAP Version |  | 8.2 Revision 3
Study: |  | HOMER CITY GENERATION
Execution: |  | Three Units Deepest Depth 12 31
Date: |  | 1/8/2026 12:32:16 PM
No. | Description |  | Unit | 1
General Cable Information
1 | Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
2 | Number of Cores |  |  | Single Core
3 | Voltage |  | [kV] | 345
4 | Conductor Area |  | [in²] | 3.9202
5 | Cable Overall Diameter |  | [in] | 6.0332
6 | Maximum Steady-State Conductor Temperature |  | [°C] | 90
7 | Maximum Emergency Conductor Temperature |  | [°C] | 110
Conductor
8 | Material |  |  | Copper
9 | Electrical Resistivity at 20°C |  | [µΩ.cm] | 1.7241
10 | Temperature Coefficient at 20°C |  | [1/K] | 0.00393
11 | Reciprocal of Temperature Coefficient of Resistance (BETA) |  | [K] | 234.4529
12 | Volumetric Specific Heat (SH) |  | [J/(K*cm³)] | 3.45
13 | Construction |  |  | 6 Segments
14 | Conductor Insulation System |  |  | Extruded
15 | Milliken Wires Construction |  |  | Bare Unidirectional Wires
16 | Ks (Skin Effect Coefficient) |  |  | 0.62
17 | Kp (Proximity Effect Coefficient) |  |  | 0.37
18 | Diameter |  | [in] | 2.48
Conductor Shield
19 | Thickness |  | [in] | 0.067
20 | Diameter |  | [in] | 2.614
Insulation
21 | Material |  |  | XLPE Unfilled
22 | Thermal Resistivity |  | [K.m/W] | 3.5
23 | Dielectric Loss Factor - ( tan delta ) |  |  | 0.001
24 | Relative Permittivity - ( epsilon ) |  |  | 2.5
25 | Specific Insulation Resistance Constant at 60°F - ( K ) |  | [㏁.1000ft] | 1858.0608
26 | Thickness |  | [in] | 1.201
27 | Diameter |  | [in] | 5.016
Insulation Screen
28 | Material |  |  | Semi Conducting Screen
29 | Thickness |  | [in] | 0.067
30 | Diameter |  | [in] | 5.15
Concentric neutral/Skid wires
31 | Are Concentric Neutral Wires Around Each Core? |  |  | n/a
32 | Material |  |  | Copper
33 | Electrical Resistivity at 20°C |  | [µΩ.cm] | 1.7241
34 | Temperature Coefficient at 20°C |  | [1/K] | 0.00393
35 | Reciprocal of Temperature Coefficient of Resistance (BETA) |  | [K] | 234.5
36 | Volumetric Specific Heat (SH) |  | [J/(K*cm³)] | 3.45
37 | Wire Type |  |  | Round Wires
38 | Length of Lay |  | [in] | 0.3937
39 | Number of Wires |  |  | 82
40 | Wire Gauge |  |  | Undefined
41 | Thickness |  | [in] | 0.090598
42 | Diameter |  | [in] | 5.3312
Sheath
43 | Is Sheath Around Each Core? |  |  | n/a
44 | Material |  |  | Copper
45 | Electrical Resistivity at 20°C |  | [µΩ.cm] | 1.7241
46 | Temperature Coefficient at 20°C |  | [1/K] | 0.00393
47 | Reciprocal of Temperature Coefficient of Resistance (BETA) |  | [K] | 234.5
48 | Volumetric Specific Heat (SH) |  | [J/(K*cm³)] | 3.45
49 | Corrugation Type |  |  | Non Corrugated
50 | Thickness |  | [in] | 0.005
51 | Diameter |  | [in] | 5.3412
Jacket
52 | Material |  |  | Polyethylene
53 | Thermal Resistivity |  | [K.m/W] | 3.5
54 | Thickness |  | [in] | 0.346
55 | Diameter |  | [in] | 6.0332
No. | Description |  | Unit | 1
Specific Installation Data
56 | Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
57 | Cable Frequency |  | [Hz] | 60
58 | Sheath / Shield Bonding |  |  | Multicables 1 Point Bonded
59 | Loss Factor Constant (ALOS) |  |  | 0.3
60 | Conduit construction |  |  | PVC Duct in Concrete
61 | Conduit material thermal resistivity |  | [K.m/W] | 6
62 | Conduit filling material |  |  | Air
63 | Inner diameter of the conduit |  | [in] | 7.981
64 | Outer diameter of the conduit |  | [in] | 8.625
Cable ID : HOMER CITY 345KV 5000KCMIL JULY
Cable Title |  | HOMER CITY GEN 345KV 5000KCMIL July

## Impedances
Cable Impedances & Admittances
CYMCAP Version |  | 8.2 Revision 3
Study: |  | HOMER CITY GENERATION
Execution: |  | Three Units Deepest Depth 12 31
Date: |  | 1/8/2026 12:32:16 PM
Earth Resistivity: [Ω.m] |  | 100
Frequency: [Hz] |  | 60
Temperature
|  |  | Circuit 1 | [17 empty] | Circuit 2 | [17 empty] | Circuit 3 | [17 empty] | Circuit 4 | [17 empty] | Circuit 5 | [17 empty] | Circuit 6
|  |  | Conductor | [5 empty] | Sheath | [5 empty] | Concentric neutral/Skid wires | [5 empty] | Conductor | [5 empty] | Sheath | [5 empty] | Concentric neutral/Skid wires | [5 empty] | Conductor | [5 empty] | Sheath | [5 empty] | Concentric neutral/Skid wires | [5 empty] | Conductor | [5 empty] | Sheath | [5 empty] | Concentric neutral/Skid wires | [5 empty] | Conductor | [5 empty] | Sheath | [5 empty] | Concentric neutral/Skid wires | [5 empty] | Conductor | [5 empty] | Sheath | [5 empty] | Concentric neutral/Skid wires
|  | Phase | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C
| Temperature | [°C] | 69.7497 | 67.6543 | 65.2792 | 67.5649 | 63.4671 | 61.4043 | 68.4058 | 66.3132 | 63.9396 | 66.2222 | 62.1316 | 60.0716 | 68.4058 | 66.3132 | 63.9396 | 66.2222 | 62.1316 | 60.0716 | 76.2106 | 78.3929 | 75.9948 | 78.4733 | 73.7119 | 75.9406 | 74.4122 | 76.5897 | 74.1938 | 76.6669 | 71.9189 | 74.1427 | 74.4122 | 76.5897 | 74.1938 | 76.6669 | 71.9189 | 74.1427 | 79.3995 | 81.542 | 81.308 | 79.0028 | 79.3915 | 77.365 | 78.0426 | 80.1823 | 79.9468 | 77.6448 | 78.0347 | 76.0109 | 78.0426 | 80.1823 | 79.9468 | 77.6448 | 78.0347 | 76.0109 | 82.4468 | 85.0243 | 85.81 | 83.1238 | 82.0843 | 84.4446 | 80.6348 | 83.2067 | 83.9877 | 81.3073 | 80.273 | 82.6282 | 80.6348 | 83.2067 | 83.9877 | 81.3073 | 80.273 | 82.6282 | 76.0546 | 78.2098 | 78.5083 | 80.953 | 82.3629 | 79.9259 | 74.7023 | 76.8546 | 77.1509 | 79.5924 | 81.0021 | 78.5684 | 74.7023 | 76.8546 | 77.1509 | 79.5924 | 81.0021 | 78.5684 | 68.3759 | 66.169 | 73.0024 | 70.4938 | 72.6541 | 74.9282 | 66.5945 | 64.3924 | 71.208 | 68.7049 | 70.8634 | 73.1326 | 66.5945 | 64.3924 | 71.208 | 68.7049 | 70.8634 | 73.1326
R_Primitive [Ω/mile]
|  |  | Circuit No. 4 | [5 empty] | Circuit No. 1 | [5 empty] | Circuit No. 6 | [5 empty] | Circuit No. 3 | [5 empty] | Circuit No. 5 | [5 empty] | Circuit No. 2 | [5 empty] | Circuit No. 4 | [5 empty] | Circuit No. 1 | [5 empty] | Circuit No. 6 | [5 empty] | Circuit No. 3 | [5 empty] | Circuit No. 5 | [5 empty] | Circuit No. 2 | [5 empty] | Circuit No. 4 | [5 empty] | Circuit No. 1 | [5 empty] | Circuit No. 6 | [5 empty] | Circuit No. 3 | [5 empty] | Circuit No. 5 | [5 empty] | Circuit No. 2
|  |  | Conductor | [35 empty] | Sheath | [35 empty] | Concentric neutral/Skid wires
|  | Phase | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C
Circuit No. 4 | Conductor | A | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 1 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11497 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 6 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 3 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 5 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 2 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 4 | Sheath | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 1 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.71767 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 6 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 3 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 5 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 2 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.73066 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 4 | Concentric neutral Skid wires | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 1 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.2233 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 6 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 3 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 5 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 2 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 4.3095
X Primitive [Ω/mile]
|  |  | Circuit No. 4 | [5 empty] | Circuit No. 1 | [5 empty] | Circuit No. 6 | [5 empty] | Circuit No. 3 | [5 empty] | Circuit No. 5 | [5 empty] | Circuit No. 2 | [5 empty] | Circuit No. 4 | [5 empty] | Circuit No. 1 | [5 empty] | Circuit No. 6 | [5 empty] | Circuit No. 3 | [5 empty] | Circuit No. 5 | [5 empty] | Circuit No. 2 | [5 empty] | Circuit No. 4 | [5 empty] | Circuit No. 1 | [5 empty] | Circuit No. 6 | [5 empty] | Circuit No. 3 | [5 empty] | Circuit No. 5 | [5 empty] | Circuit No. 2
|  |  | Conductor | [35 empty] | Sheath | [35 empty] | Concentric neutral/Skid wires
|  | Phase | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C
Circuit No. 4 | Conductor | A | 1.2685 | 0.96265 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.85155 | 0.84253 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.65626 | 0.65587 | 0.61183 | 0.61202 | 0.61875 | 0.61896 | 0.62632 | 0.62608 | 0.58481 | 0.58493 | 0.59032 | 0.59045 | 0.59609 | 0.59623 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.85155 | 0.84253 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.65626 | 0.65587 | 0.61183 | 0.61202 | 0.61875 | 0.61896 | 0.62632 | 0.62608 | 0.58481 | 0.58493 | 0.59032 | 0.59045 | 0.59609 | 0.59623 | 1.1474 | 0.96265 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.85155 | 0.84253 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.65626 | 0.65587 | 0.61183 | 0.61202 | 0.61875 | 0.61896 | 0.62632 | 0.62608 | 0.58481 | 0.58493 | 0.59032 | 0.59045 | 0.59609 | 0.59623
|  | A | 0.96265 | 1.2685 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.84253 | 0.85155 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.65587 | 0.65626 | 0.61202 | 0.61183 | 0.61896 | 0.61875 | 0.62608 | 0.62632 | 0.58493 | 0.58481 | 0.59045 | 0.59032 | 0.59623 | 0.59609 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.84253 | 0.85155 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.65587 | 0.65626 | 0.61202 | 0.61183 | 0.61896 | 0.61875 | 0.62608 | 0.62632 | 0.58493 | 0.58481 | 0.59045 | 0.59032 | 0.59623 | 0.59609 | 0.96265 | 1.1474 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.84253 | 0.85155 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.65587 | 0.65626 | 0.61202 | 0.61183 | 0.61896 | 0.61875 | 0.62608 | 0.62632 | 0.58493 | 0.58481 | 0.59045 | 0.59032 | 0.59623 | 0.59609
|  | B | 0.9206 | 0.96265 | 1.2685 | 0.96265 | 0.9206 | 0.96265 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.80593 | 0.8107 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.62991 | 0.63016 | 0.63826 | 0.63797 | 0.64658 | 0.64691 | 0.60545 | 0.60528 | 0.61202 | 0.61183 | 0.61875 | 0.61896 | 0.57965 | 0.57954 | 0.58493 | 0.58481 | 0.59045 | 0.59032 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.80593 | 0.8107 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.62991 | 0.63016 | 0.63826 | 0.63797 | 0.64658 | 0.64691 | 0.60545 | 0.60528 | 0.61202 | 0.61183 | 0.61875 | 0.61896 | 0.57965 | 0.57954 | 0.58493 | 0.58481 | 0.59045 | 0.59032 | 0.9206 | 0.96265 | 1.1474 | 0.96265 | 0.9206 | 0.96265 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.80593 | 0.8107 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.62991 | 0.63016 | 0.63826 | 0.63797 | 0.64658 | 0.64691 | 0.60545 | 0.60528 | 0.61202 | 0.61183 | 0.61875 | 0.61896 | 0.57965 | 0.57954 | 0.58493 | 0.58481 | 0.59045 | 0.59032
|  | B | 0.96265 | 0.9206 | 0.96265 | 1.2685 | 0.96265 | 0.9206 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.8107 | 0.80593 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.63016 | 0.62991 | 0.63797 | 0.63826 | 0.64691 | 0.64658 | 0.60528 | 0.60545 | 0.61183 | 0.61202 | 0.61896 | 0.61875 | 0.57954 | 0.57965 | 0.58481 | 0.58493 | 0.59032 | 0.59045 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.8107 | 0.80593 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.63016 | 0.62991 | 0.63797 | 0.63826 | 0.64691 | 0.64658 | 0.60528 | 0.60545 | 0.61183 | 0.61202 | 0.61896 | 0.61875 | 0.57954 | 0.57965 | 0.58481 | 0.58493 | 0.59032 | 0.59045 | 0.96265 | 0.9206 | 0.96265 | 1.1474 | 0.96265 | 0.9206 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.8107 | 0.80593 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.63016 | 0.62991 | 0.63797 | 0.63826 | 0.64691 | 0.64658 | 0.60528 | 0.60545 | 0.61183 | 0.61202 | 0.61896 | 0.61875 | 0.57954 | 0.57965 | 0.58481 | 0.58493 | 0.59032 | 0.59045
|  | C | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 1.2685 | 0.96265 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.78019 | 0.77726 | 0.66077 | 0.66119 | 0.67176 | 0.67126 | 0.68333 | 0.68273 | 0.62257 | 0.62235 | 0.62991 | 0.63016 | 0.63823 | 0.63795 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61202 | 0.61183 | 0.57449 | 0.57459 | 0.57954 | 0.57965 | 0.58481 | 0.58493 | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.78019 | 0.77726 | 0.66077 | 0.66119 | 0.67176 | 0.67126 | 0.68333 | 0.68273 | 0.62257 | 0.62235 | 0.62991 | 0.63016 | 0.63823 | 0.63795 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61202 | 0.61183 | 0.57449 | 0.57459 | 0.57954 | 0.57965 | 0.58481 | 0.58493 | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 1.1474 | 0.96265 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.78019 | 0.77726 | 0.66077 | 0.66119 | 0.67176 | 0.67126 | 0.68333 | 0.68273 | 0.62257 | 0.62235 | 0.62991 | 0.63016 | 0.63823 | 0.63795 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61202 | 0.61183 | 0.57449 | 0.57459 | 0.57954 | 0.57965 | 0.58481 | 0.58493
|  | C | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 0.96265 | 1.2685 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.77726 | 0.78019 | 0.66119 | 0.66077 | 0.67126 | 0.67176 | 0.68273 | 0.68333 | 0.62235 | 0.62257 | 0.63016 | 0.62991 | 0.63795 | 0.63823 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61183 | 0.61202 | 0.57459 | 0.57449 | 0.57965 | 0.57954 | 0.58493 | 0.58481 | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.77726 | 0.78019 | 0.66119 | 0.66077 | 0.67126 | 0.67176 | 0.68273 | 0.68333 | 0.62235 | 0.62257 | 0.63016 | 0.62991 | 0.63795 | 0.63823 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61183 | 0.61202 | 0.57459 | 0.57449 | 0.57965 | 0.57954 | 0.58493 | 0.58481 | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 0.96265 | 1.1474 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.77726 | 0.78019 | 0.66119 | 0.66077 | 0.67126 | 0.67176 | 0.68273 | 0.68333 | 0.62235 | 0.62257 | 0.63016 | 0.62991 | 0.63795 | 0.63823 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61183 | 0.61202 | 0.57459 | 0.57449 | 0.57965 | 0.57954 | 0.58493 | 0.58481
Circuit No. 1 |  | A | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73419 | 0.73562 | 1.2685 | 0.96265 | 0.9206 | 0.96265 | 0.86516 | 0.87874 | 0.75583 | 0.75386 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.70944 | 0.71038 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66592 | 0.66638 | 0.61199 | 0.61181 | 0.61893 | 0.61872 | 0.6263 | 0.62606 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73419 | 0.73562 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.86516 | 0.87874 | 0.75583 | 0.75386 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.70944 | 0.71038 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66592 | 0.66638 | 0.61199 | 0.61181 | 0.61893 | 0.61872 | 0.6263 | 0.62606 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73419 | 0.73562 | 1.1474 | 0.96265 | 0.9206 | 0.96265 | 0.86516 | 0.87874 | 0.75583 | 0.75386 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.70944 | 0.71038 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66592 | 0.66638 | 0.61199 | 0.61181 | 0.61893 | 0.61872 | 0.6263 | 0.62606
|  | A | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73562 | 0.73419 | 0.96265 | 1.2685 | 0.96265 | 0.9206 | 0.87874 | 0.86516 | 0.75386 | 0.75583 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.71038 | 0.70944 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66638 | 0.66592 | 0.61181 | 0.61199 | 0.61872 | 0.61893 | 0.62606 | 0.6263 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73562 | 0.73419 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.87874 | 0.86516 | 0.75386 | 0.75583 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.71038 | 0.70944 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66638 | 0.66592 | 0.61181 | 0.61199 | 0.61872 | 0.61893 | 0.62606 | 0.6263 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73562 | 0.73419 | 0.96265 | 1.1474 | 0.96265 | 0.9206 | 0.87874 | 0.86516 | 0.75386 | 0.75583 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.71038 | 0.70944 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66638 | 0.66592 | 0.61181 | 0.61199 | 0.61872 | 0.61893 | 0.62606 | 0.6263
|  | B | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.9206 | 0.96265 | 1.2685 | 0.96265 | 0.96305 | 0.9208 | 0.73413 | 0.73555 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69608 | 0.69534 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65626 | 0.65587 | 0.60526 | 0.60543 | 0.61181 | 0.61199 | 0.61872 | 0.61893 | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.96305 | 0.9208 | 0.73413 | 0.73555 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69608 | 0.69534 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65626 | 0.65587 | 0.60526 | 0.60543 | 0.61181 | 0.61199 | 0.61872 | 0.61893 | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.9206 | 0.96265 | 1.1474 | 0.96265 | 0.96305 | 0.9208 | 0.73413 | 0.73555 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69608 | 0.69534 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65626 | 0.65587 | 0.60526 | 0.60543 | 0.61181 | 0.61199 | 0.61872 | 0.61893
|  | B | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.96265 | 0.9206 | 0.96265 | 1.2685 | 0.9208 | 0.96305 | 0.73555 | 0.73413 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69534 | 0.69608 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65587 | 0.65626 | 0.60543 | 0.60526 | 0.61199 | 0.61181 | 0.61893 | 0.61872 | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.9208 | 0.96305 | 0.73555 | 0.73413 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69534 | 0.69608 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65587 | 0.65626 | 0.60543 | 0.60526 | 0.61199 | 0.61181 | 0.61893 | 0.61872 | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.96265 | 0.9206 | 0.96265 | 1.1474 | 0.9208 | 0.96305 | 0.73555 | 0.73413 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69534 | 0.69608 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65587 | 0.65626 | 0.60543 | 0.60526 | 0.61199 | 0.61181 | 0.61893 | 0.61872
|  | C | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 1.2685 | 0.96265 | 0.71717 | 0.71824 | 0.73562 | 0.73419 | 0.7559 | 0.75393 | 0.66123 | 0.66081 | 0.67129 | 0.6718 | 0.68333 | 0.68273 | 0.62991 | 0.63016 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61183 | 0.61202 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 1.1452 | 0.96265 | 0.71717 | 0.71824 | 0.73562 | 0.73419 | 0.7559 | 0.75393 | 0.66123 | 0.66081 | 0.67129 | 0.6718 | 0.68333 | 0.68273 | 0.62991 | 0.63016 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61183 | 0.61202 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 1.1474 | 0.96265 | 0.71717 | 0.71824 | 0.73562 | 0.73419 | 0.7559 | 0.75393 | 0.66123 | 0.66081 | 0.67129 | 0.6718 | 0.68333 | 0.68273 | 0.62991 | 0.63016 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61183 | 0.61202
|  | C | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 0.96265 | 1.2685 | 0.71824 | 0.71717 | 0.73419 | 0.73562 | 0.75393 | 0.7559 | 0.66081 | 0.66123 | 0.6718 | 0.67129 | 0.68273 | 0.68333 | 0.63016 | 0.62991 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61202 | 0.61183 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 0.96265 | 1.1452 | 0.71824 | 0.71717 | 0.73419 | 0.73562 | 0.75393 | 0.7559 | 0.66081 | 0.66123 | 0.6718 | 0.67129 | 0.68273 | 0.68333 | 0.63016 | 0.62991 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61202 | 0.61183 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 0.96265 | 1.1474 | 0.71824 | 0.71717 | 0.73419 | 0.73562 | 0.75393 | 0.7559 | 0.66081 | 0.66123 | 0.6718 | 0.67129 | 0.68273 | 0.68333 | 0.63016 | 0.62991 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61202 | 0.61183
Circuit No. 6 |  | A | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66077 | 0.66119 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 0.71717 | 0.71824 | 1.2685 | 0.96265 | 0.9206 | 0.96265 | 0.86501 | 0.87854 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.84253 | 0.85155 | 0.71043 | 0.70949 | 0.72664 | 0.72542 | 0.7437 | 0.74537 | 0.65626 | 0.65587 | 0.66638 | 0.66592 | 0.67743 | 0.67688 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66077 | 0.66119 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 0.71717 | 0.71824 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.86501 | 0.87854 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.84253 | 0.85155 | 0.71043 | 0.70949 | 0.72664 | 0.72542 | 0.7437 | 0.74537 | 0.65626 | 0.65587 | 0.66638 | 0.66592 | 0.67743 | 0.67688 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66077 | 0.66119 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 0.71717 | 0.71824 | 1.1474 | 0.96265 | 0.9206 | 0.96265 | 0.86501 | 0.87854 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.84253 | 0.85155 | 0.71043 | 0.70949 | 0.72664 | 0.72542 | 0.7437 | 0.74537 | 0.65626 | 0.65587 | 0.66638 | 0.66592 | 0.67743 | 0.67688
|  | A | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66119 | 0.66077 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.71824 | 0.71717 | 0.96265 | 1.2685 | 0.96265 | 0.9206 | 0.87854 | 0.86501 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.85155 | 0.84253 | 0.70949 | 0.71043 | 0.72542 | 0.72664 | 0.74537 | 0.7437 | 0.65587 | 0.65626 | 0.66592 | 0.66638 | 0.67688 | 0.67743 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66119 | 0.66077 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.71824 | 0.71717 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.87854 | 0.86501 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.85155 | 0.84253 | 0.70949 | 0.71043 | 0.72542 | 0.72664 | 0.74537 | 0.7437 | 0.65587 | 0.65626 | 0.66592 | 0.66638 | 0.67688 | 0.67743 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66119 | 0.66077 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.71824 | 0.71717 | 0.96265 | 1.1474 | 0.96265 | 0.9206 | 0.87854 | 0.86501 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.85155 | 0.84253 | 0.70949 | 0.71043 | 0.72542 | 0.72664 | 0.74537 | 0.7437 | 0.65587 | 0.65626 | 0.66592 | 0.66638 | 0.67688 | 0.67743
|  | B | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.73562 | 0.73419 | 0.9206 | 0.96265 | 1.2685 | 0.96265 | 0.96265 | 0.9206 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.8107 | 0.80593 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.72664 | 0.72542 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66592 | 0.66638 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.73562 | 0.73419 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.96265 | 0.9206 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.8107 | 0.80593 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.72664 | 0.72542 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66592 | 0.66638 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.73562 | 0.73419 | 0.9206 | 0.96265 | 1.1474 | 0.96265 | 0.96265 | 0.9206 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.8107 | 0.80593 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.72664 | 0.72542 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66592 | 0.66638
|  | B | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.73419 | 0.73562 | 0.96265 | 0.9206 | 0.96265 | 1.2685 | 0.9206 | 0.96265 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.80593 | 0.8107 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.72542 | 0.72664 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66638 | 0.66592 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.73419 | 0.73562 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.9206 | 0.96265 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.80593 | 0.8107 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.72542 | 0.72664 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66638 | 0.66592 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.73419 | 0.73562 | 0.96265 | 0.9206 | 0.96265 | 1.1474 | 0.9206 | 0.96265 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.80593 | 0.8107 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.72542 | 0.72664 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66638 | 0.66592
|  | C | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.7559 | 0.75393 | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 1.2685 | 0.96265 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.78019 | 0.77726 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.71043 | 0.70949 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.7559 | 0.75393 | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 1.1452 | 0.96265 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.78019 | 0.77726 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.71043 | 0.70949 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.7559 | 0.75393 | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 1.1474 | 0.96265 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.78019 | 0.77726 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.71043 | 0.70949 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65587 | 0.65626
|  | C | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.75393 | 0.7559 | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 0.96265 | 1.2685 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.77726 | 0.78019 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.70949 | 0.71043 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.75393 | 0.7559 | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 0.96265 | 1.1452 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.77726 | 0.78019 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.70949 | 0.71043 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.75393 | 0.7559 | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 0.96265 | 1.1474 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.77726 | 0.78019 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.70949 | 0.71043 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65626 | 0.65587
Circuit No. 3 |  | A | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.62257 | 0.62235 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66123 | 0.66081 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73562 | 0.73419 | 1.2685 | 0.96265 | 0.9206 | 0.96265 | 0.87874 | 0.86516 | 0.80593 | 0.8107 | 0.84253 | 0.85155 | 0.91358 | 0.89123 | 0.70944 | 0.71038 | 0.72536 | 0.72659 | 0.74364 | 0.7453 | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.62257 | 0.62235 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66123 | 0.66081 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73562 | 0.73419 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.87874 | 0.86516 | 0.80593 | 0.8107 | 0.84253 | 0.85155 | 0.91358 | 0.89123 | 0.70944 | 0.71038 | 0.72536 | 0.72659 | 0.74364 | 0.7453 | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.62257 | 0.62235 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66123 | 0.66081 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73562 | 0.73419 | 1.1474 | 0.96265 | 0.9206 | 0.96265 | 0.87874 | 0.86516 | 0.80593 | 0.8107 | 0.84253 | 0.85155 | 0.91358 | 0.89123 | 0.70944 | 0.71038 | 0.72536 | 0.72659 | 0.74364 | 0.7453
|  | A | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.62235 | 0.62257 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66081 | 0.66123 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73419 | 0.73562 | 0.96265 | 1.2685 | 0.96265 | 0.9206 | 0.86516 | 0.87874 | 0.8107 | 0.80593 | 0.85155 | 0.84253 | 0.89123 | 0.91358 | 0.71038 | 0.70944 | 0.72659 | 0.72536 | 0.7453 | 0.74364 | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.62235 | 0.62257 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66081 | 0.66123 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73419 | 0.73562 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.86516 | 0.87874 | 0.8107 | 0.80593 | 0.85155 | 0.84253 | 0.89123 | 0.91358 | 0.71038 | 0.70944 | 0.72659 | 0.72536 | 0.7453 | 0.74364 | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.62235 | 0.62257 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66081 | 0.66123 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73419 | 0.73562 | 0.96265 | 1.1474 | 0.96265 | 0.9206 | 0.86516 | 0.87874 | 0.8107 | 0.80593 | 0.85155 | 0.84253 | 0.89123 | 0.91358 | 0.71038 | 0.70944 | 0.72659 | 0.72536 | 0.7453 | 0.74364
|  | B | 0.64661 | 0.64694 | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67129 | 0.6718 | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.75393 | 0.7559 | 0.9206 | 0.96265 | 1.2685 | 0.96265 | 0.9208 | 0.96305 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.84253 | 0.85155 | 0.69608 | 0.69534 | 0.71038 | 0.70944 | 0.72659 | 0.72536 | 0.64661 | 0.64694 | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67129 | 0.6718 | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.75393 | 0.7559 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.9208 | 0.96305 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.84253 | 0.85155 | 0.69608 | 0.69534 | 0.71038 | 0.70944 | 0.72659 | 0.72536 | 0.64661 | 0.64694 | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67129 | 0.6718 | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.75393 | 0.7559 | 0.9206 | 0.96265 | 1.1474 | 0.96265 | 0.9208 | 0.96305 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.84253 | 0.85155 | 0.69608 | 0.69534 | 0.71038 | 0.70944 | 0.72659 | 0.72536
|  | B | 0.64694 | 0.64661 | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.6718 | 0.67129 | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.7559 | 0.75393 | 0.96265 | 0.9206 | 0.96265 | 1.2685 | 0.96305 | 0.9208 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.85155 | 0.84253 | 0.69534 | 0.69608 | 0.70944 | 0.71038 | 0.72536 | 0.72659 | 0.64694 | 0.64661 | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.6718 | 0.67129 | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.7559 | 0.75393 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.96305 | 0.9208 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.85155 | 0.84253 | 0.69534 | 0.69608 | 0.70944 | 0.71038 | 0.72536 | 0.72659 | 0.64694 | 0.64661 | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.6718 | 0.67129 | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.7559 | 0.75393 | 0.96265 | 0.9206 | 0.96265 | 1.1474 | 0.96305 | 0.9208 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.85155 | 0.84253 | 0.69534 | 0.69608 | 0.70944 | 0.71038 | 0.72536 | 0.72659
|  | C | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68333 | 0.68273 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 1.2685 | 0.96265 | 0.75393 | 0.7559 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68333 | 0.68273 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 1.1452 | 0.96265 | 0.75393 | 0.7559 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68333 | 0.68273 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 1.1474 | 0.96265 | 0.75393 | 0.7559 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.70949 | 0.71043
|  | C | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68273 | 0.68333 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 0.96265 | 1.2685 | 0.7559 | 0.75393 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68273 | 0.68333 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 0.96265 | 1.1452 | 0.7559 | 0.75393 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68273 | 0.68333 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 0.96265 | 1.1474 | 0.7559 | 0.75393 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.71043 | 0.70949
Circuit No. 5 |  | A | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.59907 | 0.59922 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.62991 | 0.63016 | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68273 | 0.68333 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.75393 | 0.7559 | 1.2685 | 0.96265 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.85155 | 0.84253 | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.59907 | 0.59922 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.62991 | 0.63016 | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68273 | 0.68333 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.75393 | 0.7559 | 1.1452 | 0.96265 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.85155 | 0.84253 | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.59907 | 0.59922 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.62991 | 0.63016 | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68273 | 0.68333 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.75393 | 0.7559 | 1.1474 | 0.96265 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.85155 | 0.84253
|  | A | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.59922 | 0.59907 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.63016 | 0.62991 | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68333 | 0.68273 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.7559 | 0.75393 | 0.96265 | 1.2685 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.84253 | 0.85155 | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.59922 | 0.59907 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.63016 | 0.62991 | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68333 | 0.68273 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.7559 | 0.75393 | 0.96265 | 1.1452 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.84253 | 0.85155 | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.59922 | 0.59907 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.63016 | 0.62991 | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68333 | 0.68273 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.7559 | 0.75393 | 0.96265 | 1.1474 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.84253 | 0.85155
|  | B | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63797 | 0.63826 | 0.72664 | 0.72542 | 0.70949 | 0.71043 | 0.69538 | 0.69612 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77735 | 0.78028 | 0.96265 | 0.9206 | 1.2685 | 0.96265 | 0.9206 | 0.96265 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63797 | 0.63826 | 0.72664 | 0.72542 | 0.70949 | 0.71043 | 0.69538 | 0.69612 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77735 | 0.78028 | 0.96265 | 0.9206 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63797 | 0.63826 | 0.72664 | 0.72542 | 0.70949 | 0.71043 | 0.69538 | 0.69612 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77735 | 0.78028 | 0.96265 | 0.9206 | 1.1474 | 0.96265 | 0.9206 | 0.96265 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.8107 | 0.80593
|  | B | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63826 | 0.63797 | 0.72542 | 0.72664 | 0.71043 | 0.70949 | 0.69612 | 0.69538 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78028 | 0.77735 | 0.9206 | 0.96265 | 0.96265 | 1.2685 | 0.96265 | 0.9206 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63826 | 0.63797 | 0.72542 | 0.72664 | 0.71043 | 0.70949 | 0.69612 | 0.69538 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78028 | 0.77735 | 0.9206 | 0.96265 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63826 | 0.63797 | 0.72542 | 0.72664 | 0.71043 | 0.70949 | 0.69612 | 0.69538 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78028 | 0.77735 | 0.9206 | 0.96265 | 0.96265 | 1.1474 | 0.96265 | 0.9206 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.80593 | 0.8107
|  | C | 0.62632 | 0.62608 | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64694 | 0.64661 | 0.7437 | 0.74537 | 0.72664 | 0.72542 | 0.71043 | 0.70949 | 0.91358 | 0.89123 | 0.84253 | 0.85155 | 0.81081 | 0.80604 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 1.2685 | 0.96265 | 0.73413 | 0.73555 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.62632 | 0.62608 | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64694 | 0.64661 | 0.7437 | 0.74537 | 0.72664 | 0.72542 | 0.71043 | 0.70949 | 0.91358 | 0.89123 | 0.84253 | 0.85155 | 0.81081 | 0.80604 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.73413 | 0.73555 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.62632 | 0.62608 | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64694 | 0.64661 | 0.7437 | 0.74537 | 0.72664 | 0.72542 | 0.71043 | 0.70949 | 0.91358 | 0.89123 | 0.84253 | 0.85155 | 0.81081 | 0.80604 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 1.1474 | 0.96265 | 0.73413 | 0.73555 | 0.75386 | 0.75583 | 0.77726 | 0.78019
|  | C | 0.62608 | 0.62632 | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64661 | 0.64694 | 0.74537 | 0.7437 | 0.72542 | 0.72664 | 0.70949 | 0.71043 | 0.89123 | 0.91358 | 0.85155 | 0.84253 | 0.80604 | 0.81081 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 0.96265 | 1.2685 | 0.73555 | 0.73413 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.62608 | 0.62632 | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64661 | 0.64694 | 0.74537 | 0.7437 | 0.72542 | 0.72664 | 0.70949 | 0.71043 | 0.89123 | 0.91358 | 0.85155 | 0.84253 | 0.80604 | 0.81081 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.73555 | 0.73413 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.62608 | 0.62632 | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64661 | 0.64694 | 0.74537 | 0.7437 | 0.72542 | 0.72664 | 0.70949 | 0.71043 | 0.89123 | 0.91358 | 0.85155 | 0.84253 | 0.80604 | 0.81081 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 0.96265 | 1.1474 | 0.73555 | 0.73413 | 0.75583 | 0.75386 | 0.78019 | 0.77726
Circuit No. 2 |  | A | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.57449 | 0.57459 | 0.61199 | 0.61181 | 0.60526 | 0.60543 | 0.59907 | 0.59922 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63795 | 0.63823 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68273 | 0.68333 | 0.78019 | 0.77726 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 1.2685 | 0.96265 | 0.96265 | 0.9206 | 0.87854 | 0.86501 | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.57449 | 0.57459 | 0.61199 | 0.61181 | 0.60526 | 0.60543 | 0.59907 | 0.59922 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63795 | 0.63823 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68273 | 0.68333 | 0.78019 | 0.77726 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 1.1452 | 0.96265 | 0.96265 | 0.9206 | 0.87854 | 0.86501 | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.57449 | 0.57459 | 0.61199 | 0.61181 | 0.60526 | 0.60543 | 0.59907 | 0.59922 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63795 | 0.63823 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68273 | 0.68333 | 0.78019 | 0.77726 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 1.1474 | 0.96265 | 0.96265 | 0.9206 | 0.87854 | 0.86501
|  | A | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.57459 | 0.57449 | 0.61181 | 0.61199 | 0.60543 | 0.60526 | 0.59922 | 0.59907 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63823 | 0.63795 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68333 | 0.68273 | 0.77726 | 0.78019 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.96265 | 1.2685 | 0.9206 | 0.96265 | 0.86501 | 0.87854 | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.57459 | 0.57449 | 0.61181 | 0.61199 | 0.60543 | 0.60526 | 0.59922 | 0.59907 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63823 | 0.63795 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68333 | 0.68273 | 0.77726 | 0.78019 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.96265 | 1.1452 | 0.9206 | 0.96265 | 0.86501 | 0.87854 | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.57459 | 0.57449 | 0.61181 | 0.61199 | 0.60543 | 0.60526 | 0.59922 | 0.59907 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63823 | 0.63795 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68333 | 0.68273 | 0.77726 | 0.78019 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.96265 | 1.1474 | 0.9206 | 0.96265 | 0.86501 | 0.87854
|  | B | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.61893 | 0.61872 | 0.61181 | 0.61199 | 0.60528 | 0.60545 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64658 | 0.64691 | 0.72536 | 0.72659 | 0.71038 | 0.70944 | 0.69538 | 0.69612 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.96265 | 0.9206 | 1.2685 | 0.96265 | 0.96265 | 0.9206 | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.61893 | 0.61872 | 0.61181 | 0.61199 | 0.60528 | 0.60545 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64658 | 0.64691 | 0.72536 | 0.72659 | 0.71038 | 0.70944 | 0.69538 | 0.69612 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.96265 | 0.9206 | 1.1452 | 0.96265 | 0.96265 | 0.9206 | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.61893 | 0.61872 | 0.61181 | 0.61199 | 0.60528 | 0.60545 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64658 | 0.64691 | 0.72536 | 0.72659 | 0.71038 | 0.70944 | 0.69538 | 0.69612 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.96265 | 0.9206 | 1.1474 | 0.96265 | 0.96265 | 0.9206
|  | B | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.61872 | 0.61893 | 0.61199 | 0.61181 | 0.60545 | 0.60528 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64691 | 0.64658 | 0.72659 | 0.72536 | 0.70944 | 0.71038 | 0.69612 | 0.69538 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.9206 | 0.96265 | 0.96265 | 1.2685 | 0.9206 | 0.96265 | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.61872 | 0.61893 | 0.61199 | 0.61181 | 0.60545 | 0.60528 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64691 | 0.64658 | 0.72659 | 0.72536 | 0.70944 | 0.71038 | 0.69612 | 0.69538 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.9206 | 0.96265 | 0.96265 | 1.1452 | 0.9206 | 0.96265 | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.61872 | 0.61893 | 0.61199 | 0.61181 | 0.60545 | 0.60528 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64691 | 0.64658 | 0.72659 | 0.72536 | 0.70944 | 0.71038 | 0.69612 | 0.69538 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.9206 | 0.96265 | 0.96265 | 1.1474 | 0.9206 | 0.96265
|  | C | 0.59609 | 0.59623 | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.6263 | 0.62606 | 0.61872 | 0.61893 | 0.61183 | 0.61202 | 0.67743 | 0.67688 | 0.66592 | 0.66638 | 0.65587 | 0.65626 | 0.74364 | 0.7453 | 0.72659 | 0.72536 | 0.70949 | 0.71043 | 0.85155 | 0.84253 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 1.2685 | 0.96265 | 0.59609 | 0.59623 | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.6263 | 0.62606 | 0.61872 | 0.61893 | 0.61183 | 0.61202 | 0.67743 | 0.67688 | 0.66592 | 0.66638 | 0.65587 | 0.65626 | 0.74364 | 0.7453 | 0.72659 | 0.72536 | 0.70949 | 0.71043 | 0.85155 | 0.84253 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 1.1452 | 0.96265 | 0.59609 | 0.59623 | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.6263 | 0.62606 | 0.61872 | 0.61893 | 0.61183 | 0.61202 | 0.67743 | 0.67688 | 0.66592 | 0.66638 | 0.65587 | 0.65626 | 0.74364 | 0.7453 | 0.72659 | 0.72536 | 0.70949 | 0.71043 | 0.85155 | 0.84253 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 1.1474 | 0.96265
|  | C | 0.59623 | 0.59609 | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.62606 | 0.6263 | 0.61893 | 0.61872 | 0.61202 | 0.61183 | 0.67688 | 0.67743 | 0.66638 | 0.66592 | 0.65626 | 0.65587 | 0.7453 | 0.74364 | 0.72536 | 0.72659 | 0.71043 | 0.70949 | 0.84253 | 0.85155 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 0.96265 | 1.2685 | 0.59623 | 0.59609 | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.62606 | 0.6263 | 0.61893 | 0.61872 | 0.61202 | 0.61183 | 0.67688 | 0.67743 | 0.66638 | 0.66592 | 0.65626 | 0.65587 | 0.7453 | 0.74364 | 0.72536 | 0.72659 | 0.71043 | 0.70949 | 0.84253 | 0.85155 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 0.96265 | 1.1452 | 0.59623 | 0.59609 | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.62606 | 0.6263 | 0.61893 | 0.61872 | 0.61202 | 0.61183 | 0.67688 | 0.67743 | 0.66638 | 0.66592 | 0.65626 | 0.65587 | 0.7453 | 0.74364 | 0.72536 | 0.72659 | 0.71043 | 0.70949 | 0.84253 | 0.85155 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 0.96265 | 1.1474
Circuit No. 4 | Sheath | A | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.85155 | 0.84253 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.65626 | 0.65587 | 0.61183 | 0.61202 | 0.61875 | 0.61896 | 0.62632 | 0.62608 | 0.58481 | 0.58493 | 0.59032 | 0.59045 | 0.59609 | 0.59623 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.85155 | 0.84253 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.65626 | 0.65587 | 0.61183 | 0.61202 | 0.61875 | 0.61896 | 0.62632 | 0.62608 | 0.58481 | 0.58493 | 0.59032 | 0.59045 | 0.59609 | 0.59623 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.85155 | 0.84253 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.65626 | 0.65587 | 0.61183 | 0.61202 | 0.61875 | 0.61896 | 0.62632 | 0.62608 | 0.58481 | 0.58493 | 0.59032 | 0.59045 | 0.59609 | 0.59623
|  | A | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.84253 | 0.85155 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.65587 | 0.65626 | 0.61202 | 0.61183 | 0.61896 | 0.61875 | 0.62608 | 0.62632 | 0.58493 | 0.58481 | 0.59045 | 0.59032 | 0.59623 | 0.59609 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.84253 | 0.85155 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.65587 | 0.65626 | 0.61202 | 0.61183 | 0.61896 | 0.61875 | 0.62608 | 0.62632 | 0.58493 | 0.58481 | 0.59045 | 0.59032 | 0.59623 | 0.59609 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.84253 | 0.85155 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.65587 | 0.65626 | 0.61202 | 0.61183 | 0.61896 | 0.61875 | 0.62608 | 0.62632 | 0.58493 | 0.58481 | 0.59045 | 0.59032 | 0.59623 | 0.59609
|  | B | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.80593 | 0.8107 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.62991 | 0.63016 | 0.63826 | 0.63797 | 0.64658 | 0.64691 | 0.60545 | 0.60528 | 0.61202 | 0.61183 | 0.61875 | 0.61896 | 0.57965 | 0.57954 | 0.58493 | 0.58481 | 0.59045 | 0.59032 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.80593 | 0.8107 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.62991 | 0.63016 | 0.63826 | 0.63797 | 0.64658 | 0.64691 | 0.60545 | 0.60528 | 0.61202 | 0.61183 | 0.61875 | 0.61896 | 0.57965 | 0.57954 | 0.58493 | 0.58481 | 0.59045 | 0.59032 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.80593 | 0.8107 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.62991 | 0.63016 | 0.63826 | 0.63797 | 0.64658 | 0.64691 | 0.60545 | 0.60528 | 0.61202 | 0.61183 | 0.61875 | 0.61896 | 0.57965 | 0.57954 | 0.58493 | 0.58481 | 0.59045 | 0.59032
|  | B | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.8107 | 0.80593 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.63016 | 0.62991 | 0.63797 | 0.63826 | 0.64691 | 0.64658 | 0.60528 | 0.60545 | 0.61183 | 0.61202 | 0.61896 | 0.61875 | 0.57954 | 0.57965 | 0.58481 | 0.58493 | 0.59032 | 0.59045 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.8107 | 0.80593 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.63016 | 0.62991 | 0.63797 | 0.63826 | 0.64691 | 0.64658 | 0.60528 | 0.60545 | 0.61183 | 0.61202 | 0.61896 | 0.61875 | 0.57954 | 0.57965 | 0.58481 | 0.58493 | 0.59032 | 0.59045 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.8107 | 0.80593 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.63016 | 0.62991 | 0.63797 | 0.63826 | 0.64691 | 0.64658 | 0.60528 | 0.60545 | 0.61183 | 0.61202 | 0.61896 | 0.61875 | 0.57954 | 0.57965 | 0.58481 | 0.58493 | 0.59032 | 0.59045
|  | C | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.78019 | 0.77726 | 0.66077 | 0.66119 | 0.67176 | 0.67126 | 0.68333 | 0.68273 | 0.62257 | 0.62235 | 0.62991 | 0.63016 | 0.63823 | 0.63795 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61202 | 0.61183 | 0.57449 | 0.57459 | 0.57954 | 0.57965 | 0.58481 | 0.58493 | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.78019 | 0.77726 | 0.66077 | 0.66119 | 0.67176 | 0.67126 | 0.68333 | 0.68273 | 0.62257 | 0.62235 | 0.62991 | 0.63016 | 0.63823 | 0.63795 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61202 | 0.61183 | 0.57449 | 0.57459 | 0.57954 | 0.57965 | 0.58481 | 0.58493 | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.78019 | 0.77726 | 0.66077 | 0.66119 | 0.67176 | 0.67126 | 0.68333 | 0.68273 | 0.62257 | 0.62235 | 0.62991 | 0.63016 | 0.63823 | 0.63795 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61202 | 0.61183 | 0.57449 | 0.57459 | 0.57954 | 0.57965 | 0.58481 | 0.58493
|  | C | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.77726 | 0.78019 | 0.66119 | 0.66077 | 0.67126 | 0.67176 | 0.68273 | 0.68333 | 0.62235 | 0.62257 | 0.63016 | 0.62991 | 0.63795 | 0.63823 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61183 | 0.61202 | 0.57459 | 0.57449 | 0.57965 | 0.57954 | 0.58493 | 0.58481 | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.77726 | 0.78019 | 0.66119 | 0.66077 | 0.67126 | 0.67176 | 0.68273 | 0.68333 | 0.62235 | 0.62257 | 0.63016 | 0.62991 | 0.63795 | 0.63823 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61183 | 0.61202 | 0.57459 | 0.57449 | 0.57965 | 0.57954 | 0.58493 | 0.58481 | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.77726 | 0.78019 | 0.66119 | 0.66077 | 0.67126 | 0.67176 | 0.68273 | 0.68333 | 0.62235 | 0.62257 | 0.63016 | 0.62991 | 0.63795 | 0.63823 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61183 | 0.61202 | 0.57459 | 0.57449 | 0.57965 | 0.57954 | 0.58493 | 0.58481
Circuit No. 1 |  | A | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73419 | 0.73562 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.86516 | 0.87874 | 0.75583 | 0.75386 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.70944 | 0.71038 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66592 | 0.66638 | 0.61199 | 0.61181 | 0.61893 | 0.61872 | 0.6263 | 0.62606 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73419 | 0.73562 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.86516 | 0.87874 | 0.75583 | 0.75386 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.70944 | 0.71038 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66592 | 0.66638 | 0.61199 | 0.61181 | 0.61893 | 0.61872 | 0.6263 | 0.62606 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73419 | 0.73562 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.86516 | 0.87874 | 0.75583 | 0.75386 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.70944 | 0.71038 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66592 | 0.66638 | 0.61199 | 0.61181 | 0.61893 | 0.61872 | 0.6263 | 0.62606
|  | A | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73562 | 0.73419 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.87874 | 0.86516 | 0.75386 | 0.75583 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.71038 | 0.70944 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66638 | 0.66592 | 0.61181 | 0.61199 | 0.61872 | 0.61893 | 0.62606 | 0.6263 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73562 | 0.73419 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.87874 | 0.86516 | 0.75386 | 0.75583 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.71038 | 0.70944 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66638 | 0.66592 | 0.61181 | 0.61199 | 0.61872 | 0.61893 | 0.62606 | 0.6263 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73562 | 0.73419 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.87874 | 0.86516 | 0.75386 | 0.75583 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.71038 | 0.70944 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66638 | 0.66592 | 0.61181 | 0.61199 | 0.61872 | 0.61893 | 0.62606 | 0.6263
|  | B | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.96305 | 0.9208 | 0.73413 | 0.73555 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69608 | 0.69534 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65626 | 0.65587 | 0.60526 | 0.60543 | 0.61181 | 0.61199 | 0.61872 | 0.61893 | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.96305 | 0.9208 | 0.73413 | 0.73555 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69608 | 0.69534 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65626 | 0.65587 | 0.60526 | 0.60543 | 0.61181 | 0.61199 | 0.61872 | 0.61893 | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.96305 | 0.9208 | 0.73413 | 0.73555 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69608 | 0.69534 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65626 | 0.65587 | 0.60526 | 0.60543 | 0.61181 | 0.61199 | 0.61872 | 0.61893
|  | B | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.9208 | 0.96305 | 0.73555 | 0.73413 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69534 | 0.69608 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65587 | 0.65626 | 0.60543 | 0.60526 | 0.61199 | 0.61181 | 0.61893 | 0.61872 | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.9208 | 0.96305 | 0.73555 | 0.73413 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69534 | 0.69608 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65587 | 0.65626 | 0.60543 | 0.60526 | 0.61199 | 0.61181 | 0.61893 | 0.61872 | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.9208 | 0.96305 | 0.73555 | 0.73413 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69534 | 0.69608 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65587 | 0.65626 | 0.60543 | 0.60526 | 0.61199 | 0.61181 | 0.61893 | 0.61872
|  | C | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 1.1452 | 0.96265 | 0.71717 | 0.71824 | 0.73562 | 0.73419 | 0.7559 | 0.75393 | 0.66123 | 0.66081 | 0.67129 | 0.6718 | 0.68333 | 0.68273 | 0.62991 | 0.63016 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61183 | 0.61202 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 1.1452 | 0.96265 | 0.71717 | 0.71824 | 0.73562 | 0.73419 | 0.7559 | 0.75393 | 0.66123 | 0.66081 | 0.67129 | 0.6718 | 0.68333 | 0.68273 | 0.62991 | 0.63016 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61183 | 0.61202 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 1.1452 | 0.96265 | 0.71717 | 0.71824 | 0.73562 | 0.73419 | 0.7559 | 0.75393 | 0.66123 | 0.66081 | 0.67129 | 0.6718 | 0.68333 | 0.68273 | 0.62991 | 0.63016 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61183 | 0.61202
|  | C | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 0.96265 | 1.1452 | 0.71824 | 0.71717 | 0.73419 | 0.73562 | 0.75393 | 0.7559 | 0.66081 | 0.66123 | 0.6718 | 0.67129 | 0.68273 | 0.68333 | 0.63016 | 0.62991 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61202 | 0.61183 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 0.96265 | 1.1452 | 0.71824 | 0.71717 | 0.73419 | 0.73562 | 0.75393 | 0.7559 | 0.66081 | 0.66123 | 0.6718 | 0.67129 | 0.68273 | 0.68333 | 0.63016 | 0.62991 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61202 | 0.61183 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 0.96265 | 1.1452 | 0.71824 | 0.71717 | 0.73419 | 0.73562 | 0.75393 | 0.7559 | 0.66081 | 0.66123 | 0.6718 | 0.67129 | 0.68273 | 0.68333 | 0.63016 | 0.62991 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61202 | 0.61183
Circuit No. 6 |  | A | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66077 | 0.66119 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 0.71717 | 0.71824 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.86501 | 0.87854 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.84253 | 0.85155 | 0.71043 | 0.70949 | 0.72664 | 0.72542 | 0.7437 | 0.74537 | 0.65626 | 0.65587 | 0.66638 | 0.66592 | 0.67743 | 0.67688 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66077 | 0.66119 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 0.71717 | 0.71824 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.86501 | 0.87854 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.84253 | 0.85155 | 0.71043 | 0.70949 | 0.72664 | 0.72542 | 0.7437 | 0.74537 | 0.65626 | 0.65587 | 0.66638 | 0.66592 | 0.67743 | 0.67688 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66077 | 0.66119 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 0.71717 | 0.71824 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.86501 | 0.87854 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.84253 | 0.85155 | 0.71043 | 0.70949 | 0.72664 | 0.72542 | 0.7437 | 0.74537 | 0.65626 | 0.65587 | 0.66638 | 0.66592 | 0.67743 | 0.67688
|  | A | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66119 | 0.66077 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.71824 | 0.71717 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.87854 | 0.86501 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.85155 | 0.84253 | 0.70949 | 0.71043 | 0.72542 | 0.72664 | 0.74537 | 0.7437 | 0.65587 | 0.65626 | 0.66592 | 0.66638 | 0.67688 | 0.67743 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66119 | 0.66077 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.71824 | 0.71717 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.87854 | 0.86501 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.85155 | 0.84253 | 0.70949 | 0.71043 | 0.72542 | 0.72664 | 0.74537 | 0.7437 | 0.65587 | 0.65626 | 0.66592 | 0.66638 | 0.67688 | 0.67743 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66119 | 0.66077 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.71824 | 0.71717 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.87854 | 0.86501 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.85155 | 0.84253 | 0.70949 | 0.71043 | 0.72542 | 0.72664 | 0.74537 | 0.7437 | 0.65587 | 0.65626 | 0.66592 | 0.66638 | 0.67688 | 0.67743
|  | B | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.73562 | 0.73419 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.96265 | 0.9206 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.8107 | 0.80593 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.72664 | 0.72542 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66592 | 0.66638 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.73562 | 0.73419 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.96265 | 0.9206 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.8107 | 0.80593 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.72664 | 0.72542 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66592 | 0.66638 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.73562 | 0.73419 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.96265 | 0.9206 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.8107 | 0.80593 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.72664 | 0.72542 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66592 | 0.66638
|  | B | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.73419 | 0.73562 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.9206 | 0.96265 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.80593 | 0.8107 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.72542 | 0.72664 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66638 | 0.66592 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.73419 | 0.73562 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.9206 | 0.96265 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.80593 | 0.8107 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.72542 | 0.72664 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66638 | 0.66592 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.73419 | 0.73562 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.9206 | 0.96265 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.80593 | 0.8107 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.72542 | 0.72664 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66638 | 0.66592
|  | C | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.7559 | 0.75393 | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 1.1452 | 0.96265 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.78019 | 0.77726 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.71043 | 0.70949 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.7559 | 0.75393 | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 1.1452 | 0.96265 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.78019 | 0.77726 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.71043 | 0.70949 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.7559 | 0.75393 | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 1.1452 | 0.96265 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.78019 | 0.77726 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.71043 | 0.70949 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65587 | 0.65626
|  | C | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.75393 | 0.7559 | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 0.96265 | 1.1452 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.77726 | 0.78019 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.70949 | 0.71043 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.75393 | 0.7559 | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 0.96265 | 1.1452 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.77726 | 0.78019 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.70949 | 0.71043 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.75393 | 0.7559 | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 0.96265 | 1.1452 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.77726 | 0.78019 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.70949 | 0.71043 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65626 | 0.65587
Circuit No. 3 |  | A | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.62257 | 0.62235 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66123 | 0.66081 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73562 | 0.73419 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.87874 | 0.86516 | 0.80593 | 0.8107 | 0.84253 | 0.85155 | 0.91358 | 0.89123 | 0.70944 | 0.71038 | 0.72536 | 0.72659 | 0.74364 | 0.7453 | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.62257 | 0.62235 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66123 | 0.66081 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73562 | 0.73419 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.87874 | 0.86516 | 0.80593 | 0.8107 | 0.84253 | 0.85155 | 0.91358 | 0.89123 | 0.70944 | 0.71038 | 0.72536 | 0.72659 | 0.74364 | 0.7453 | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.62257 | 0.62235 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66123 | 0.66081 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73562 | 0.73419 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.87874 | 0.86516 | 0.80593 | 0.8107 | 0.84253 | 0.85155 | 0.91358 | 0.89123 | 0.70944 | 0.71038 | 0.72536 | 0.72659 | 0.74364 | 0.7453
|  | A | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.62235 | 0.62257 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66081 | 0.66123 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73419 | 0.73562 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.86516 | 0.87874 | 0.8107 | 0.80593 | 0.85155 | 0.84253 | 0.89123 | 0.91358 | 0.71038 | 0.70944 | 0.72659 | 0.72536 | 0.7453 | 0.74364 | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.62235 | 0.62257 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66081 | 0.66123 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73419 | 0.73562 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.86516 | 0.87874 | 0.8107 | 0.80593 | 0.85155 | 0.84253 | 0.89123 | 0.91358 | 0.71038 | 0.70944 | 0.72659 | 0.72536 | 0.7453 | 0.74364 | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.62235 | 0.62257 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66081 | 0.66123 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73419 | 0.73562 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.86516 | 0.87874 | 0.8107 | 0.80593 | 0.85155 | 0.84253 | 0.89123 | 0.91358 | 0.71038 | 0.70944 | 0.72659 | 0.72536 | 0.7453 | 0.74364
|  | B | 0.64661 | 0.64694 | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67129 | 0.6718 | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.75393 | 0.7559 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.9208 | 0.96305 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.84253 | 0.85155 | 0.69608 | 0.69534 | 0.71038 | 0.70944 | 0.72659 | 0.72536 | 0.64661 | 0.64694 | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67129 | 0.6718 | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.75393 | 0.7559 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.9208 | 0.96305 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.84253 | 0.85155 | 0.69608 | 0.69534 | 0.71038 | 0.70944 | 0.72659 | 0.72536 | 0.64661 | 0.64694 | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67129 | 0.6718 | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.75393 | 0.7559 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.9208 | 0.96305 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.84253 | 0.85155 | 0.69608 | 0.69534 | 0.71038 | 0.70944 | 0.72659 | 0.72536
|  | B | 0.64694 | 0.64661 | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.6718 | 0.67129 | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.7559 | 0.75393 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.96305 | 0.9208 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.85155 | 0.84253 | 0.69534 | 0.69608 | 0.70944 | 0.71038 | 0.72536 | 0.72659 | 0.64694 | 0.64661 | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.6718 | 0.67129 | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.7559 | 0.75393 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.96305 | 0.9208 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.85155 | 0.84253 | 0.69534 | 0.69608 | 0.70944 | 0.71038 | 0.72536 | 0.72659 | 0.64694 | 0.64661 | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.6718 | 0.67129 | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.7559 | 0.75393 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.96305 | 0.9208 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.85155 | 0.84253 | 0.69534 | 0.69608 | 0.70944 | 0.71038 | 0.72536 | 0.72659
|  | C | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68333 | 0.68273 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 1.1452 | 0.96265 | 0.75393 | 0.7559 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68333 | 0.68273 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 1.1452 | 0.96265 | 0.75393 | 0.7559 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68333 | 0.68273 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 1.1452 | 0.96265 | 0.75393 | 0.7559 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.70949 | 0.71043
|  | C | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68273 | 0.68333 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 0.96265 | 1.1452 | 0.7559 | 0.75393 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68273 | 0.68333 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 0.96265 | 1.1452 | 0.7559 | 0.75393 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68273 | 0.68333 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 0.96265 | 1.1452 | 0.7559 | 0.75393 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.71043 | 0.70949
Circuit No. 5 |  | A | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.59907 | 0.59922 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.62991 | 0.63016 | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68273 | 0.68333 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.75393 | 0.7559 | 1.1452 | 0.96265 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.85155 | 0.84253 | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.59907 | 0.59922 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.62991 | 0.63016 | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68273 | 0.68333 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.75393 | 0.7559 | 1.1452 | 0.96265 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.85155 | 0.84253 | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.59907 | 0.59922 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.62991 | 0.63016 | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68273 | 0.68333 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.75393 | 0.7559 | 1.1452 | 0.96265 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.85155 | 0.84253
|  | A | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.59922 | 0.59907 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.63016 | 0.62991 | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68333 | 0.68273 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.7559 | 0.75393 | 0.96265 | 1.1452 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.84253 | 0.85155 | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.59922 | 0.59907 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.63016 | 0.62991 | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68333 | 0.68273 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.7559 | 0.75393 | 0.96265 | 1.1452 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.84253 | 0.85155 | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.59922 | 0.59907 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.63016 | 0.62991 | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68333 | 0.68273 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.7559 | 0.75393 | 0.96265 | 1.1452 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.84253 | 0.85155
|  | B | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63797 | 0.63826 | 0.72664 | 0.72542 | 0.70949 | 0.71043 | 0.69538 | 0.69612 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77735 | 0.78028 | 0.96265 | 0.9206 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63797 | 0.63826 | 0.72664 | 0.72542 | 0.70949 | 0.71043 | 0.69538 | 0.69612 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77735 | 0.78028 | 0.96265 | 0.9206 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63797 | 0.63826 | 0.72664 | 0.72542 | 0.70949 | 0.71043 | 0.69538 | 0.69612 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77735 | 0.78028 | 0.96265 | 0.9206 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.8107 | 0.80593
|  | B | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63826 | 0.63797 | 0.72542 | 0.72664 | 0.71043 | 0.70949 | 0.69612 | 0.69538 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78028 | 0.77735 | 0.9206 | 0.96265 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63826 | 0.63797 | 0.72542 | 0.72664 | 0.71043 | 0.70949 | 0.69612 | 0.69538 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78028 | 0.77735 | 0.9206 | 0.96265 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63826 | 0.63797 | 0.72542 | 0.72664 | 0.71043 | 0.70949 | 0.69612 | 0.69538 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78028 | 0.77735 | 0.9206 | 0.96265 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.80593 | 0.8107
|  | C | 0.62632 | 0.62608 | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64694 | 0.64661 | 0.7437 | 0.74537 | 0.72664 | 0.72542 | 0.71043 | 0.70949 | 0.91358 | 0.89123 | 0.84253 | 0.85155 | 0.81081 | 0.80604 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.73413 | 0.73555 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.62632 | 0.62608 | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64694 | 0.64661 | 0.7437 | 0.74537 | 0.72664 | 0.72542 | 0.71043 | 0.70949 | 0.91358 | 0.89123 | 0.84253 | 0.85155 | 0.81081 | 0.80604 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.73413 | 0.73555 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.62632 | 0.62608 | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64694 | 0.64661 | 0.7437 | 0.74537 | 0.72664 | 0.72542 | 0.71043 | 0.70949 | 0.91358 | 0.89123 | 0.84253 | 0.85155 | 0.81081 | 0.80604 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.73413 | 0.73555 | 0.75386 | 0.75583 | 0.77726 | 0.78019
|  | C | 0.62608 | 0.62632 | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64661 | 0.64694 | 0.74537 | 0.7437 | 0.72542 | 0.72664 | 0.70949 | 0.71043 | 0.89123 | 0.91358 | 0.85155 | 0.84253 | 0.80604 | 0.81081 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.73555 | 0.73413 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.62608 | 0.62632 | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64661 | 0.64694 | 0.74537 | 0.7437 | 0.72542 | 0.72664 | 0.70949 | 0.71043 | 0.89123 | 0.91358 | 0.85155 | 0.84253 | 0.80604 | 0.81081 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.73555 | 0.73413 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.62608 | 0.62632 | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64661 | 0.64694 | 0.74537 | 0.7437 | 0.72542 | 0.72664 | 0.70949 | 0.71043 | 0.89123 | 0.91358 | 0.85155 | 0.84253 | 0.80604 | 0.81081 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.73555 | 0.73413 | 0.75583 | 0.75386 | 0.78019 | 0.77726
Circuit No. 2 |  | A | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.57449 | 0.57459 | 0.61199 | 0.61181 | 0.60526 | 0.60543 | 0.59907 | 0.59922 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63795 | 0.63823 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68273 | 0.68333 | 0.78019 | 0.77726 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 1.1452 | 0.96265 | 0.96265 | 0.9206 | 0.87854 | 0.86501 | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.57449 | 0.57459 | 0.61199 | 0.61181 | 0.60526 | 0.60543 | 0.59907 | 0.59922 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63795 | 0.63823 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68273 | 0.68333 | 0.78019 | 0.77726 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 1.1452 | 0.96265 | 0.96265 | 0.9206 | 0.87854 | 0.86501 | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.57449 | 0.57459 | 0.61199 | 0.61181 | 0.60526 | 0.60543 | 0.59907 | 0.59922 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63795 | 0.63823 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68273 | 0.68333 | 0.78019 | 0.77726 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 1.1452 | 0.96265 | 0.96265 | 0.9206 | 0.87854 | 0.86501
|  | A | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.57459 | 0.57449 | 0.61181 | 0.61199 | 0.60543 | 0.60526 | 0.59922 | 0.59907 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63823 | 0.63795 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68333 | 0.68273 | 0.77726 | 0.78019 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.96265 | 1.1452 | 0.9206 | 0.96265 | 0.86501 | 0.87854 | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.57459 | 0.57449 | 0.61181 | 0.61199 | 0.60543 | 0.60526 | 0.59922 | 0.59907 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63823 | 0.63795 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68333 | 0.68273 | 0.77726 | 0.78019 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.96265 | 1.1452 | 0.9206 | 0.96265 | 0.86501 | 0.87854 | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.57459 | 0.57449 | 0.61181 | 0.61199 | 0.60543 | 0.60526 | 0.59922 | 0.59907 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63823 | 0.63795 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68333 | 0.68273 | 0.77726 | 0.78019 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.96265 | 1.1452 | 0.9206 | 0.96265 | 0.86501 | 0.87854
|  | B | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.61893 | 0.61872 | 0.61181 | 0.61199 | 0.60528 | 0.60545 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64658 | 0.64691 | 0.72536 | 0.72659 | 0.71038 | 0.70944 | 0.69538 | 0.69612 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.96265 | 0.9206 | 1.1452 | 0.96265 | 0.96265 | 0.9206 | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.61893 | 0.61872 | 0.61181 | 0.61199 | 0.60528 | 0.60545 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64658 | 0.64691 | 0.72536 | 0.72659 | 0.71038 | 0.70944 | 0.69538 | 0.69612 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.96265 | 0.9206 | 1.1452 | 0.96265 | 0.96265 | 0.9206 | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.61893 | 0.61872 | 0.61181 | 0.61199 | 0.60528 | 0.60545 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64658 | 0.64691 | 0.72536 | 0.72659 | 0.71038 | 0.70944 | 0.69538 | 0.69612 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.96265 | 0.9206 | 1.1452 | 0.96265 | 0.96265 | 0.9206
|  | B | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.61872 | 0.61893 | 0.61199 | 0.61181 | 0.60545 | 0.60528 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64691 | 0.64658 | 0.72659 | 0.72536 | 0.70944 | 0.71038 | 0.69612 | 0.69538 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.9206 | 0.96265 | 0.96265 | 1.1452 | 0.9206 | 0.96265 | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.61872 | 0.61893 | 0.61199 | 0.61181 | 0.60545 | 0.60528 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64691 | 0.64658 | 0.72659 | 0.72536 | 0.70944 | 0.71038 | 0.69612 | 0.69538 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.9206 | 0.96265 | 0.96265 | 1.1452 | 0.9206 | 0.96265 | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.61872 | 0.61893 | 0.61199 | 0.61181 | 0.60545 | 0.60528 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64691 | 0.64658 | 0.72659 | 0.72536 | 0.70944 | 0.71038 | 0.69612 | 0.69538 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.9206 | 0.96265 | 0.96265 | 1.1452 | 0.9206 | 0.96265
|  | C | 0.59609 | 0.59623 | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.6263 | 0.62606 | 0.61872 | 0.61893 | 0.61183 | 0.61202 | 0.67743 | 0.67688 | 0.66592 | 0.66638 | 0.65587 | 0.65626 | 0.74364 | 0.7453 | 0.72659 | 0.72536 | 0.70949 | 0.71043 | 0.85155 | 0.84253 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 1.1452 | 0.96265 | 0.59609 | 0.59623 | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.6263 | 0.62606 | 0.61872 | 0.61893 | 0.61183 | 0.61202 | 0.67743 | 0.67688 | 0.66592 | 0.66638 | 0.65587 | 0.65626 | 0.74364 | 0.7453 | 0.72659 | 0.72536 | 0.70949 | 0.71043 | 0.85155 | 0.84253 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 1.1452 | 0.96265 | 0.59609 | 0.59623 | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.6263 | 0.62606 | 0.61872 | 0.61893 | 0.61183 | 0.61202 | 0.67743 | 0.67688 | 0.66592 | 0.66638 | 0.65587 | 0.65626 | 0.74364 | 0.7453 | 0.72659 | 0.72536 | 0.70949 | 0.71043 | 0.85155 | 0.84253 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 1.1452 | 0.96265
|  | C | 0.59623 | 0.59609 | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.62606 | 0.6263 | 0.61893 | 0.61872 | 0.61202 | 0.61183 | 0.67688 | 0.67743 | 0.66638 | 0.66592 | 0.65626 | 0.65587 | 0.7453 | 0.74364 | 0.72536 | 0.72659 | 0.71043 | 0.70949 | 0.84253 | 0.85155 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 0.96265 | 1.1452 | 0.59623 | 0.59609 | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.62606 | 0.6263 | 0.61893 | 0.61872 | 0.61202 | 0.61183 | 0.67688 | 0.67743 | 0.66638 | 0.66592 | 0.65626 | 0.65587 | 0.7453 | 0.74364 | 0.72536 | 0.72659 | 0.71043 | 0.70949 | 0.84253 | 0.85155 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 0.96265 | 1.1452 | 0.59623 | 0.59609 | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.62606 | 0.6263 | 0.61893 | 0.61872 | 0.61202 | 0.61183 | 0.67688 | 0.67743 | 0.66638 | 0.66592 | 0.65626 | 0.65587 | 0.7453 | 0.74364 | 0.72536 | 0.72659 | 0.71043 | 0.70949 | 0.84253 | 0.85155 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 0.96265 | 1.1452
Circuit No. 4 | Concentric neutral Skid wires | A | 1.1474 | 0.96265 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.85155 | 0.84253 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.65626 | 0.65587 | 0.61183 | 0.61202 | 0.61875 | 0.61896 | 0.62632 | 0.62608 | 0.58481 | 0.58493 | 0.59032 | 0.59045 | 0.59609 | 0.59623 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.85155 | 0.84253 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.65626 | 0.65587 | 0.61183 | 0.61202 | 0.61875 | 0.61896 | 0.62632 | 0.62608 | 0.58481 | 0.58493 | 0.59032 | 0.59045 | 0.59609 | 0.59623 | 1.1472 | 0.96265 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.85155 | 0.84253 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.65626 | 0.65587 | 0.61183 | 0.61202 | 0.61875 | 0.61896 | 0.62632 | 0.62608 | 0.58481 | 0.58493 | 0.59032 | 0.59045 | 0.59609 | 0.59623
|  | A | 0.96265 | 1.1474 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.84253 | 0.85155 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.65587 | 0.65626 | 0.61202 | 0.61183 | 0.61896 | 0.61875 | 0.62608 | 0.62632 | 0.58493 | 0.58481 | 0.59045 | 0.59032 | 0.59623 | 0.59609 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.84253 | 0.85155 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.65587 | 0.65626 | 0.61202 | 0.61183 | 0.61896 | 0.61875 | 0.62608 | 0.62632 | 0.58493 | 0.58481 | 0.59045 | 0.59032 | 0.59623 | 0.59609 | 0.96265 | 1.1472 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.84253 | 0.85155 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.65587 | 0.65626 | 0.61202 | 0.61183 | 0.61896 | 0.61875 | 0.62608 | 0.62632 | 0.58493 | 0.58481 | 0.59045 | 0.59032 | 0.59623 | 0.59609
|  | B | 0.9206 | 0.96265 | 1.1474 | 0.96265 | 0.9206 | 0.96265 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.80593 | 0.8107 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.62991 | 0.63016 | 0.63826 | 0.63797 | 0.64658 | 0.64691 | 0.60545 | 0.60528 | 0.61202 | 0.61183 | 0.61875 | 0.61896 | 0.57965 | 0.57954 | 0.58493 | 0.58481 | 0.59045 | 0.59032 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.80593 | 0.8107 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.62991 | 0.63016 | 0.63826 | 0.63797 | 0.64658 | 0.64691 | 0.60545 | 0.60528 | 0.61202 | 0.61183 | 0.61875 | 0.61896 | 0.57965 | 0.57954 | 0.58493 | 0.58481 | 0.59045 | 0.59032 | 0.9206 | 0.96265 | 1.1472 | 0.96265 | 0.9206 | 0.96265 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.80593 | 0.8107 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.62991 | 0.63016 | 0.63826 | 0.63797 | 0.64658 | 0.64691 | 0.60545 | 0.60528 | 0.61202 | 0.61183 | 0.61875 | 0.61896 | 0.57965 | 0.57954 | 0.58493 | 0.58481 | 0.59045 | 0.59032
|  | B | 0.96265 | 0.9206 | 0.96265 | 1.1474 | 0.96265 | 0.9206 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.8107 | 0.80593 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.63016 | 0.62991 | 0.63797 | 0.63826 | 0.64691 | 0.64658 | 0.60528 | 0.60545 | 0.61183 | 0.61202 | 0.61896 | 0.61875 | 0.57954 | 0.57965 | 0.58481 | 0.58493 | 0.59032 | 0.59045 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.8107 | 0.80593 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.63016 | 0.62991 | 0.63797 | 0.63826 | 0.64691 | 0.64658 | 0.60528 | 0.60545 | 0.61183 | 0.61202 | 0.61896 | 0.61875 | 0.57954 | 0.57965 | 0.58481 | 0.58493 | 0.59032 | 0.59045 | 0.96265 | 0.9206 | 0.96265 | 1.1472 | 0.96265 | 0.9206 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.8107 | 0.80593 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.63016 | 0.62991 | 0.63797 | 0.63826 | 0.64691 | 0.64658 | 0.60528 | 0.60545 | 0.61183 | 0.61202 | 0.61896 | 0.61875 | 0.57954 | 0.57965 | 0.58481 | 0.58493 | 0.59032 | 0.59045
|  | C | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 1.1474 | 0.96265 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.78019 | 0.77726 | 0.66077 | 0.66119 | 0.67176 | 0.67126 | 0.68333 | 0.68273 | 0.62257 | 0.62235 | 0.62991 | 0.63016 | 0.63823 | 0.63795 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61202 | 0.61183 | 0.57449 | 0.57459 | 0.57954 | 0.57965 | 0.58481 | 0.58493 | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.78019 | 0.77726 | 0.66077 | 0.66119 | 0.67176 | 0.67126 | 0.68333 | 0.68273 | 0.62257 | 0.62235 | 0.62991 | 0.63016 | 0.63823 | 0.63795 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61202 | 0.61183 | 0.57449 | 0.57459 | 0.57954 | 0.57965 | 0.58481 | 0.58493 | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 1.1472 | 0.96265 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.78019 | 0.77726 | 0.66077 | 0.66119 | 0.67176 | 0.67126 | 0.68333 | 0.68273 | 0.62257 | 0.62235 | 0.62991 | 0.63016 | 0.63823 | 0.63795 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61202 | 0.61183 | 0.57449 | 0.57459 | 0.57954 | 0.57965 | 0.58481 | 0.58493
|  | C | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 0.96265 | 1.1474 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.77726 | 0.78019 | 0.66119 | 0.66077 | 0.67126 | 0.67176 | 0.68273 | 0.68333 | 0.62235 | 0.62257 | 0.63016 | 0.62991 | 0.63795 | 0.63823 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61183 | 0.61202 | 0.57459 | 0.57449 | 0.57965 | 0.57954 | 0.58493 | 0.58481 | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.77726 | 0.78019 | 0.66119 | 0.66077 | 0.67126 | 0.67176 | 0.68273 | 0.68333 | 0.62235 | 0.62257 | 0.63016 | 0.62991 | 0.63795 | 0.63823 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61183 | 0.61202 | 0.57459 | 0.57449 | 0.57965 | 0.57954 | 0.58493 | 0.58481 | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 0.96265 | 1.1472 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.77726 | 0.78019 | 0.66119 | 0.66077 | 0.67126 | 0.67176 | 0.68273 | 0.68333 | 0.62235 | 0.62257 | 0.63016 | 0.62991 | 0.63795 | 0.63823 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61183 | 0.61202 | 0.57459 | 0.57449 | 0.57965 | 0.57954 | 0.58493 | 0.58481
Circuit No. 1 |  | A | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73419 | 0.73562 | 1.1474 | 0.96265 | 0.9206 | 0.96265 | 0.86516 | 0.87874 | 0.75583 | 0.75386 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.70944 | 0.71038 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66592 | 0.66638 | 0.61199 | 0.61181 | 0.61893 | 0.61872 | 0.6263 | 0.62606 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73419 | 0.73562 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.86516 | 0.87874 | 0.75583 | 0.75386 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.70944 | 0.71038 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66592 | 0.66638 | 0.61199 | 0.61181 | 0.61893 | 0.61872 | 0.6263 | 0.62606 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73419 | 0.73562 | 1.1472 | 0.96265 | 0.9206 | 0.96265 | 0.86516 | 0.87874 | 0.75583 | 0.75386 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.70944 | 0.71038 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66592 | 0.66638 | 0.61199 | 0.61181 | 0.61893 | 0.61872 | 0.6263 | 0.62606
|  | A | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73562 | 0.73419 | 0.96265 | 1.1474 | 0.96265 | 0.9206 | 0.87874 | 0.86516 | 0.75386 | 0.75583 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.71038 | 0.70944 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66638 | 0.66592 | 0.61181 | 0.61199 | 0.61872 | 0.61893 | 0.62606 | 0.6263 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73562 | 0.73419 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.87874 | 0.86516 | 0.75386 | 0.75583 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.71038 | 0.70944 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66638 | 0.66592 | 0.61181 | 0.61199 | 0.61872 | 0.61893 | 0.62606 | 0.6263 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73562 | 0.73419 | 0.96265 | 1.1472 | 0.96265 | 0.9206 | 0.87874 | 0.86516 | 0.75386 | 0.75583 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.71038 | 0.70944 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66638 | 0.66592 | 0.61181 | 0.61199 | 0.61872 | 0.61893 | 0.62606 | 0.6263
|  | B | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.9206 | 0.96265 | 1.1474 | 0.96265 | 0.96305 | 0.9208 | 0.73413 | 0.73555 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69608 | 0.69534 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65626 | 0.65587 | 0.60526 | 0.60543 | 0.61181 | 0.61199 | 0.61872 | 0.61893 | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.96305 | 0.9208 | 0.73413 | 0.73555 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69608 | 0.69534 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65626 | 0.65587 | 0.60526 | 0.60543 | 0.61181 | 0.61199 | 0.61872 | 0.61893 | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.9206 | 0.96265 | 1.1472 | 0.96265 | 0.96305 | 0.9208 | 0.73413 | 0.73555 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69608 | 0.69534 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65626 | 0.65587 | 0.60526 | 0.60543 | 0.61181 | 0.61199 | 0.61872 | 0.61893
|  | B | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.96265 | 0.9206 | 0.96265 | 1.1474 | 0.9208 | 0.96305 | 0.73555 | 0.73413 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69534 | 0.69608 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65587 | 0.65626 | 0.60543 | 0.60526 | 0.61199 | 0.61181 | 0.61893 | 0.61872 | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.9208 | 0.96305 | 0.73555 | 0.73413 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69534 | 0.69608 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65587 | 0.65626 | 0.60543 | 0.60526 | 0.61199 | 0.61181 | 0.61893 | 0.61872 | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.96265 | 0.9206 | 0.96265 | 1.1472 | 0.9208 | 0.96305 | 0.73555 | 0.73413 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69534 | 0.69608 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65587 | 0.65626 | 0.60543 | 0.60526 | 0.61199 | 0.61181 | 0.61893 | 0.61872
|  | C | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 1.1474 | 0.96265 | 0.71717 | 0.71824 | 0.73562 | 0.73419 | 0.7559 | 0.75393 | 0.66123 | 0.66081 | 0.67129 | 0.6718 | 0.68333 | 0.68273 | 0.62991 | 0.63016 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61183 | 0.61202 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 1.1452 | 0.96265 | 0.71717 | 0.71824 | 0.73562 | 0.73419 | 0.7559 | 0.75393 | 0.66123 | 0.66081 | 0.67129 | 0.6718 | 0.68333 | 0.68273 | 0.62991 | 0.63016 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61183 | 0.61202 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 1.1472 | 0.96265 | 0.71717 | 0.71824 | 0.73562 | 0.73419 | 0.7559 | 0.75393 | 0.66123 | 0.66081 | 0.67129 | 0.6718 | 0.68333 | 0.68273 | 0.62991 | 0.63016 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61183 | 0.61202
|  | C | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 0.96265 | 1.1474 | 0.71824 | 0.71717 | 0.73419 | 0.73562 | 0.75393 | 0.7559 | 0.66081 | 0.66123 | 0.6718 | 0.67129 | 0.68273 | 0.68333 | 0.63016 | 0.62991 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61202 | 0.61183 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 0.96265 | 1.1452 | 0.71824 | 0.71717 | 0.73419 | 0.73562 | 0.75393 | 0.7559 | 0.66081 | 0.66123 | 0.6718 | 0.67129 | 0.68273 | 0.68333 | 0.63016 | 0.62991 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61202 | 0.61183 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 0.96265 | 1.1472 | 0.71824 | 0.71717 | 0.73419 | 0.73562 | 0.75393 | 0.7559 | 0.66081 | 0.66123 | 0.6718 | 0.67129 | 0.68273 | 0.68333 | 0.63016 | 0.62991 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61202 | 0.61183
Circuit No. 6 |  | A | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66077 | 0.66119 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 0.71717 | 0.71824 | 1.1474 | 0.96265 | 0.9206 | 0.96265 | 0.86501 | 0.87854 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.84253 | 0.85155 | 0.71043 | 0.70949 | 0.72664 | 0.72542 | 0.7437 | 0.74537 | 0.65626 | 0.65587 | 0.66638 | 0.66592 | 0.67743 | 0.67688 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66077 | 0.66119 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 0.71717 | 0.71824 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.86501 | 0.87854 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.84253 | 0.85155 | 0.71043 | 0.70949 | 0.72664 | 0.72542 | 0.7437 | 0.74537 | 0.65626 | 0.65587 | 0.66638 | 0.66592 | 0.67743 | 0.67688 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66077 | 0.66119 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 0.71717 | 0.71824 | 1.1472 | 0.96265 | 0.9206 | 0.96265 | 0.86501 | 0.87854 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.84253 | 0.85155 | 0.71043 | 0.70949 | 0.72664 | 0.72542 | 0.7437 | 0.74537 | 0.65626 | 0.65587 | 0.66638 | 0.66592 | 0.67743 | 0.67688
|  | A | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66119 | 0.66077 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.71824 | 0.71717 | 0.96265 | 1.1474 | 0.96265 | 0.9206 | 0.87854 | 0.86501 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.85155 | 0.84253 | 0.70949 | 0.71043 | 0.72542 | 0.72664 | 0.74537 | 0.7437 | 0.65587 | 0.65626 | 0.66592 | 0.66638 | 0.67688 | 0.67743 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66119 | 0.66077 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.71824 | 0.71717 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.87854 | 0.86501 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.85155 | 0.84253 | 0.70949 | 0.71043 | 0.72542 | 0.72664 | 0.74537 | 0.7437 | 0.65587 | 0.65626 | 0.66592 | 0.66638 | 0.67688 | 0.67743 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66119 | 0.66077 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.71824 | 0.71717 | 0.96265 | 1.1472 | 0.96265 | 0.9206 | 0.87854 | 0.86501 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.85155 | 0.84253 | 0.70949 | 0.71043 | 0.72542 | 0.72664 | 0.74537 | 0.7437 | 0.65587 | 0.65626 | 0.66592 | 0.66638 | 0.67688 | 0.67743
|  | B | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.73562 | 0.73419 | 0.9206 | 0.96265 | 1.1474 | 0.96265 | 0.96265 | 0.9206 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.8107 | 0.80593 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.72664 | 0.72542 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66592 | 0.66638 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.73562 | 0.73419 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.96265 | 0.9206 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.8107 | 0.80593 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.72664 | 0.72542 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66592 | 0.66638 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.73562 | 0.73419 | 0.9206 | 0.96265 | 1.1472 | 0.96265 | 0.96265 | 0.9206 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.8107 | 0.80593 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.72664 | 0.72542 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66592 | 0.66638
|  | B | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.73419 | 0.73562 | 0.96265 | 0.9206 | 0.96265 | 1.1474 | 0.9206 | 0.96265 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.80593 | 0.8107 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.72542 | 0.72664 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66638 | 0.66592 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.73419 | 0.73562 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.9206 | 0.96265 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.80593 | 0.8107 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.72542 | 0.72664 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66638 | 0.66592 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.73419 | 0.73562 | 0.96265 | 0.9206 | 0.96265 | 1.1472 | 0.9206 | 0.96265 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.80593 | 0.8107 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.72542 | 0.72664 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66638 | 0.66592
|  | C | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.7559 | 0.75393 | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 1.1474 | 0.96265 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.78019 | 0.77726 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.71043 | 0.70949 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.7559 | 0.75393 | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 1.1452 | 0.96265 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.78019 | 0.77726 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.71043 | 0.70949 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.7559 | 0.75393 | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 1.1472 | 0.96265 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.78019 | 0.77726 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.71043 | 0.70949 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65587 | 0.65626
|  | C | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.75393 | 0.7559 | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 0.96265 | 1.1474 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.77726 | 0.78019 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.70949 | 0.71043 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.75393 | 0.7559 | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 0.96265 | 1.1452 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.77726 | 0.78019 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.70949 | 0.71043 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.75393 | 0.7559 | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 0.96265 | 1.1472 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.77726 | 0.78019 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.70949 | 0.71043 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65626 | 0.65587
Circuit No. 3 |  | A | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.62257 | 0.62235 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66123 | 0.66081 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73562 | 0.73419 | 1.1474 | 0.96265 | 0.9206 | 0.96265 | 0.87874 | 0.86516 | 0.80593 | 0.8107 | 0.84253 | 0.85155 | 0.91358 | 0.89123 | 0.70944 | 0.71038 | 0.72536 | 0.72659 | 0.74364 | 0.7453 | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.62257 | 0.62235 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66123 | 0.66081 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73562 | 0.73419 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.87874 | 0.86516 | 0.80593 | 0.8107 | 0.84253 | 0.85155 | 0.91358 | 0.89123 | 0.70944 | 0.71038 | 0.72536 | 0.72659 | 0.74364 | 0.7453 | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.62257 | 0.62235 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66123 | 0.66081 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73562 | 0.73419 | 1.1472 | 0.96265 | 0.9206 | 0.96265 | 0.87874 | 0.86516 | 0.80593 | 0.8107 | 0.84253 | 0.85155 | 0.91358 | 0.89123 | 0.70944 | 0.71038 | 0.72536 | 0.72659 | 0.74364 | 0.7453
|  | A | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.62235 | 0.62257 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66081 | 0.66123 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73419 | 0.73562 | 0.96265 | 1.1474 | 0.96265 | 0.9206 | 0.86516 | 0.87874 | 0.8107 | 0.80593 | 0.85155 | 0.84253 | 0.89123 | 0.91358 | 0.71038 | 0.70944 | 0.72659 | 0.72536 | 0.7453 | 0.74364 | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.62235 | 0.62257 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66081 | 0.66123 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73419 | 0.73562 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.86516 | 0.87874 | 0.8107 | 0.80593 | 0.85155 | 0.84253 | 0.89123 | 0.91358 | 0.71038 | 0.70944 | 0.72659 | 0.72536 | 0.7453 | 0.74364 | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.62235 | 0.62257 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66081 | 0.66123 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73419 | 0.73562 | 0.96265 | 1.1472 | 0.96265 | 0.9206 | 0.86516 | 0.87874 | 0.8107 | 0.80593 | 0.85155 | 0.84253 | 0.89123 | 0.91358 | 0.71038 | 0.70944 | 0.72659 | 0.72536 | 0.7453 | 0.74364
|  | B | 0.64661 | 0.64694 | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67129 | 0.6718 | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.75393 | 0.7559 | 0.9206 | 0.96265 | 1.1474 | 0.96265 | 0.9208 | 0.96305 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.84253 | 0.85155 | 0.69608 | 0.69534 | 0.71038 | 0.70944 | 0.72659 | 0.72536 | 0.64661 | 0.64694 | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67129 | 0.6718 | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.75393 | 0.7559 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.9208 | 0.96305 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.84253 | 0.85155 | 0.69608 | 0.69534 | 0.71038 | 0.70944 | 0.72659 | 0.72536 | 0.64661 | 0.64694 | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67129 | 0.6718 | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.75393 | 0.7559 | 0.9206 | 0.96265 | 1.1472 | 0.96265 | 0.9208 | 0.96305 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.84253 | 0.85155 | 0.69608 | 0.69534 | 0.71038 | 0.70944 | 0.72659 | 0.72536
|  | B | 0.64694 | 0.64661 | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.6718 | 0.67129 | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.7559 | 0.75393 | 0.96265 | 0.9206 | 0.96265 | 1.1474 | 0.96305 | 0.9208 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.85155 | 0.84253 | 0.69534 | 0.69608 | 0.70944 | 0.71038 | 0.72536 | 0.72659 | 0.64694 | 0.64661 | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.6718 | 0.67129 | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.7559 | 0.75393 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.96305 | 0.9208 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.85155 | 0.84253 | 0.69534 | 0.69608 | 0.70944 | 0.71038 | 0.72536 | 0.72659 | 0.64694 | 0.64661 | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.6718 | 0.67129 | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.7559 | 0.75393 | 0.96265 | 0.9206 | 0.96265 | 1.1472 | 0.96305 | 0.9208 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.85155 | 0.84253 | 0.69534 | 0.69608 | 0.70944 | 0.71038 | 0.72536 | 0.72659
|  | C | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68333 | 0.68273 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 1.1474 | 0.96265 | 0.75393 | 0.7559 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68333 | 0.68273 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 1.1452 | 0.96265 | 0.75393 | 0.7559 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68333 | 0.68273 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 1.1472 | 0.96265 | 0.75393 | 0.7559 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.70949 | 0.71043
|  | C | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68273 | 0.68333 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 0.96265 | 1.1474 | 0.7559 | 0.75393 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68273 | 0.68333 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 0.96265 | 1.1452 | 0.7559 | 0.75393 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68273 | 0.68333 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 0.96265 | 1.1472 | 0.7559 | 0.75393 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.71043 | 0.70949
Circuit No. 5 |  | A | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.59907 | 0.59922 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.62991 | 0.63016 | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68273 | 0.68333 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.75393 | 0.7559 | 1.1474 | 0.96265 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.85155 | 0.84253 | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.59907 | 0.59922 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.62991 | 0.63016 | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68273 | 0.68333 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.75393 | 0.7559 | 1.1452 | 0.96265 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.85155 | 0.84253 | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.59907 | 0.59922 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.62991 | 0.63016 | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68273 | 0.68333 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.75393 | 0.7559 | 1.1472 | 0.96265 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.85155 | 0.84253
|  | A | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.59922 | 0.59907 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.63016 | 0.62991 | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68333 | 0.68273 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.7559 | 0.75393 | 0.96265 | 1.1474 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.84253 | 0.85155 | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.59922 | 0.59907 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.63016 | 0.62991 | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68333 | 0.68273 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.7559 | 0.75393 | 0.96265 | 1.1452 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.84253 | 0.85155 | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.59922 | 0.59907 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.63016 | 0.62991 | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68333 | 0.68273 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.7559 | 0.75393 | 0.96265 | 1.1472 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.84253 | 0.85155
|  | B | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63797 | 0.63826 | 0.72664 | 0.72542 | 0.70949 | 0.71043 | 0.69538 | 0.69612 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77735 | 0.78028 | 0.96265 | 0.9206 | 1.1474 | 0.96265 | 0.9206 | 0.96265 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63797 | 0.63826 | 0.72664 | 0.72542 | 0.70949 | 0.71043 | 0.69538 | 0.69612 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77735 | 0.78028 | 0.96265 | 0.9206 | 1.1452 | 0.96265 | 0.9206 | 0.96265 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63797 | 0.63826 | 0.72664 | 0.72542 | 0.70949 | 0.71043 | 0.69538 | 0.69612 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77735 | 0.78028 | 0.96265 | 0.9206 | 1.1472 | 0.96265 | 0.9206 | 0.96265 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.8107 | 0.80593
|  | B | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63826 | 0.63797 | 0.72542 | 0.72664 | 0.71043 | 0.70949 | 0.69612 | 0.69538 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78028 | 0.77735 | 0.9206 | 0.96265 | 0.96265 | 1.1474 | 0.96265 | 0.9206 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63826 | 0.63797 | 0.72542 | 0.72664 | 0.71043 | 0.70949 | 0.69612 | 0.69538 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78028 | 0.77735 | 0.9206 | 0.96265 | 0.96265 | 1.1452 | 0.96265 | 0.9206 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63826 | 0.63797 | 0.72542 | 0.72664 | 0.71043 | 0.70949 | 0.69612 | 0.69538 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78028 | 0.77735 | 0.9206 | 0.96265 | 0.96265 | 1.1472 | 0.96265 | 0.9206 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.80593 | 0.8107
|  | C | 0.62632 | 0.62608 | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64694 | 0.64661 | 0.7437 | 0.74537 | 0.72664 | 0.72542 | 0.71043 | 0.70949 | 0.91358 | 0.89123 | 0.84253 | 0.85155 | 0.81081 | 0.80604 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 1.1474 | 0.96265 | 0.73413 | 0.73555 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.62632 | 0.62608 | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64694 | 0.64661 | 0.7437 | 0.74537 | 0.72664 | 0.72542 | 0.71043 | 0.70949 | 0.91358 | 0.89123 | 0.84253 | 0.85155 | 0.81081 | 0.80604 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 1.1452 | 0.96265 | 0.73413 | 0.73555 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.62632 | 0.62608 | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64694 | 0.64661 | 0.7437 | 0.74537 | 0.72664 | 0.72542 | 0.71043 | 0.70949 | 0.91358 | 0.89123 | 0.84253 | 0.85155 | 0.81081 | 0.80604 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 1.1472 | 0.96265 | 0.73413 | 0.73555 | 0.75386 | 0.75583 | 0.77726 | 0.78019
|  | C | 0.62608 | 0.62632 | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64661 | 0.64694 | 0.74537 | 0.7437 | 0.72542 | 0.72664 | 0.70949 | 0.71043 | 0.89123 | 0.91358 | 0.85155 | 0.84253 | 0.80604 | 0.81081 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 0.96265 | 1.1474 | 0.73555 | 0.73413 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.62608 | 0.62632 | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64661 | 0.64694 | 0.74537 | 0.7437 | 0.72542 | 0.72664 | 0.70949 | 0.71043 | 0.89123 | 0.91358 | 0.85155 | 0.84253 | 0.80604 | 0.81081 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 0.96265 | 1.1452 | 0.73555 | 0.73413 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.62608 | 0.62632 | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64661 | 0.64694 | 0.74537 | 0.7437 | 0.72542 | 0.72664 | 0.70949 | 0.71043 | 0.89123 | 0.91358 | 0.85155 | 0.84253 | 0.80604 | 0.81081 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 0.96265 | 1.1472 | 0.73555 | 0.73413 | 0.75583 | 0.75386 | 0.78019 | 0.77726
Circuit No. 2 |  | A | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.57449 | 0.57459 | 0.61199 | 0.61181 | 0.60526 | 0.60543 | 0.59907 | 0.59922 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63795 | 0.63823 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68273 | 0.68333 | 0.78019 | 0.77726 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 1.1474 | 0.96265 | 0.96265 | 0.9206 | 0.87854 | 0.86501 | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.57449 | 0.57459 | 0.61199 | 0.61181 | 0.60526 | 0.60543 | 0.59907 | 0.59922 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63795 | 0.63823 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68273 | 0.68333 | 0.78019 | 0.77726 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 1.1452 | 0.96265 | 0.96265 | 0.9206 | 0.87854 | 0.86501 | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.57449 | 0.57459 | 0.61199 | 0.61181 | 0.60526 | 0.60543 | 0.59907 | 0.59922 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63795 | 0.63823 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68273 | 0.68333 | 0.78019 | 0.77726 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 1.1472 | 0.96265 | 0.96265 | 0.9206 | 0.87854 | 0.86501
|  | A | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.57459 | 0.57449 | 0.61181 | 0.61199 | 0.60543 | 0.60526 | 0.59922 | 0.59907 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63823 | 0.63795 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68333 | 0.68273 | 0.77726 | 0.78019 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.96265 | 1.1474 | 0.9206 | 0.96265 | 0.86501 | 0.87854 | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.57459 | 0.57449 | 0.61181 | 0.61199 | 0.60543 | 0.60526 | 0.59922 | 0.59907 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63823 | 0.63795 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68333 | 0.68273 | 0.77726 | 0.78019 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.96265 | 1.1452 | 0.9206 | 0.96265 | 0.86501 | 0.87854 | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.57459 | 0.57449 | 0.61181 | 0.61199 | 0.60543 | 0.60526 | 0.59922 | 0.59907 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63823 | 0.63795 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68333 | 0.68273 | 0.77726 | 0.78019 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.96265 | 1.1472 | 0.9206 | 0.96265 | 0.86501 | 0.87854
|  | B | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.61893 | 0.61872 | 0.61181 | 0.61199 | 0.60528 | 0.60545 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64658 | 0.64691 | 0.72536 | 0.72659 | 0.71038 | 0.70944 | 0.69538 | 0.69612 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.96265 | 0.9206 | 1.1474 | 0.96265 | 0.96265 | 0.9206 | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.61893 | 0.61872 | 0.61181 | 0.61199 | 0.60528 | 0.60545 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64658 | 0.64691 | 0.72536 | 0.72659 | 0.71038 | 0.70944 | 0.69538 | 0.69612 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.96265 | 0.9206 | 1.1452 | 0.96265 | 0.96265 | 0.9206 | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.61893 | 0.61872 | 0.61181 | 0.61199 | 0.60528 | 0.60545 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64658 | 0.64691 | 0.72536 | 0.72659 | 0.71038 | 0.70944 | 0.69538 | 0.69612 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.96265 | 0.9206 | 1.1472 | 0.96265 | 0.96265 | 0.9206
|  | B | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.61872 | 0.61893 | 0.61199 | 0.61181 | 0.60545 | 0.60528 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64691 | 0.64658 | 0.72659 | 0.72536 | 0.70944 | 0.71038 | 0.69612 | 0.69538 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.9206 | 0.96265 | 0.96265 | 1.1474 | 0.9206 | 0.96265 | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.61872 | 0.61893 | 0.61199 | 0.61181 | 0.60545 | 0.60528 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64691 | 0.64658 | 0.72659 | 0.72536 | 0.70944 | 0.71038 | 0.69612 | 0.69538 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.9206 | 0.96265 | 0.96265 | 1.1452 | 0.9206 | 0.96265 | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.61872 | 0.61893 | 0.61199 | 0.61181 | 0.60545 | 0.60528 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64691 | 0.64658 | 0.72659 | 0.72536 | 0.70944 | 0.71038 | 0.69612 | 0.69538 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.9206 | 0.96265 | 0.96265 | 1.1472 | 0.9206 | 0.96265
|  | C | 0.59609 | 0.59623 | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.6263 | 0.62606 | 0.61872 | 0.61893 | 0.61183 | 0.61202 | 0.67743 | 0.67688 | 0.66592 | 0.66638 | 0.65587 | 0.65626 | 0.74364 | 0.7453 | 0.72659 | 0.72536 | 0.70949 | 0.71043 | 0.85155 | 0.84253 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 1.1474 | 0.96265 | 0.59609 | 0.59623 | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.6263 | 0.62606 | 0.61872 | 0.61893 | 0.61183 | 0.61202 | 0.67743 | 0.67688 | 0.66592 | 0.66638 | 0.65587 | 0.65626 | 0.74364 | 0.7453 | 0.72659 | 0.72536 | 0.70949 | 0.71043 | 0.85155 | 0.84253 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 1.1452 | 0.96265 | 0.59609 | 0.59623 | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.6263 | 0.62606 | 0.61872 | 0.61893 | 0.61183 | 0.61202 | 0.67743 | 0.67688 | 0.66592 | 0.66638 | 0.65587 | 0.65626 | 0.74364 | 0.7453 | 0.72659 | 0.72536 | 0.70949 | 0.71043 | 0.85155 | 0.84253 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 1.1472 | 0.96265
|  | C | 0.59623 | 0.59609 | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.62606 | 0.6263 | 0.61893 | 0.61872 | 0.61202 | 0.61183 | 0.67688 | 0.67743 | 0.66638 | 0.66592 | 0.65626 | 0.65587 | 0.7453 | 0.74364 | 0.72536 | 0.72659 | 0.71043 | 0.70949 | 0.84253 | 0.85155 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 0.96265 | 1.1474 | 0.59623 | 0.59609 | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.62606 | 0.6263 | 0.61893 | 0.61872 | 0.61202 | 0.61183 | 0.67688 | 0.67743 | 0.66638 | 0.66592 | 0.65626 | 0.65587 | 0.7453 | 0.74364 | 0.72536 | 0.72659 | 0.71043 | 0.70949 | 0.84253 | 0.85155 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 0.96265 | 1.1452 | 0.59623 | 0.59609 | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.62606 | 0.6263 | 0.61893 | 0.61872 | 0.61202 | 0.61183 | 0.67688 | 0.67743 | 0.66638 | 0.66592 | 0.65626 | 0.65587 | 0.7453 | 0.74364 | 0.72536 | 0.72659 | 0.71043 | 0.70949 | 0.84253 | 0.85155 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 0.96265 | 1.1472
R Bonding [Ω/mile]
|  |  | Circuit No. 4 | [5 empty] | Circuit No. 1 | [5 empty] | Circuit No. 6 | [5 empty] | Circuit No. 3 | [5 empty] | Circuit No. 5 | [5 empty] | Circuit No. 2
Conductor
|  | Phase | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C
Circuit No. 4 | Conductor | A | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 1 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11497 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 6 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 3 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 5 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 2 |  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302
|  | B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302
|  | C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517
X Bonding [Ω/mile]
|  |  | Circuit No. 4 | [5 empty] | Circuit No. 1 | [5 empty] | Circuit No. 6 | [5 empty] | Circuit No. 3 | [5 empty] | Circuit No. 5 | [5 empty] | Circuit No. 2
Conductor
|  | Phase | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C
Circuit No. 4 | Conductor | A | 1.2685 | 0.96265 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.85155 | 0.84253 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.65626 | 0.65587 | 0.61183 | 0.61202 | 0.61875 | 0.61896 | 0.62632 | 0.62608 | 0.58481 | 0.58493 | 0.59032 | 0.59045 | 0.59609 | 0.59623
|  | A | 0.96265 | 1.2685 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.84253 | 0.85155 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.65587 | 0.65626 | 0.61202 | 0.61183 | 0.61896 | 0.61875 | 0.62608 | 0.62632 | 0.58493 | 0.58481 | 0.59045 | 0.59032 | 0.59623 | 0.59609
|  | B | 0.9206 | 0.96265 | 1.2685 | 0.96265 | 0.9206 | 0.96265 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.80593 | 0.8107 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.62991 | 0.63016 | 0.63826 | 0.63797 | 0.64658 | 0.64691 | 0.60545 | 0.60528 | 0.61202 | 0.61183 | 0.61875 | 0.61896 | 0.57965 | 0.57954 | 0.58493 | 0.58481 | 0.59045 | 0.59032
|  | B | 0.96265 | 0.9206 | 0.96265 | 1.2685 | 0.96265 | 0.9206 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.8107 | 0.80593 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.63016 | 0.62991 | 0.63797 | 0.63826 | 0.64691 | 0.64658 | 0.60528 | 0.60545 | 0.61183 | 0.61202 | 0.61896 | 0.61875 | 0.57954 | 0.57965 | 0.58481 | 0.58493 | 0.59032 | 0.59045
|  | C | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 1.2685 | 0.96265 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.78019 | 0.77726 | 0.66077 | 0.66119 | 0.67176 | 0.67126 | 0.68333 | 0.68273 | 0.62257 | 0.62235 | 0.62991 | 0.63016 | 0.63823 | 0.63795 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61202 | 0.61183 | 0.57449 | 0.57459 | 0.57954 | 0.57965 | 0.58481 | 0.58493
|  | C | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 0.96265 | 1.2685 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.77726 | 0.78019 | 0.66119 | 0.66077 | 0.67126 | 0.67176 | 0.68273 | 0.68333 | 0.62235 | 0.62257 | 0.63016 | 0.62991 | 0.63795 | 0.63823 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61183 | 0.61202 | 0.57459 | 0.57449 | 0.57965 | 0.57954 | 0.58493 | 0.58481
Circuit No. 1 |  | A | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73419 | 0.73562 | 1.2685 | 0.96265 | 0.9206 | 0.96265 | 0.86516 | 0.87874 | 0.75583 | 0.75386 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.70944 | 0.71038 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66592 | 0.66638 | 0.61199 | 0.61181 | 0.61893 | 0.61872 | 0.6263 | 0.62606
|  | A | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73562 | 0.73419 | 0.96265 | 1.2685 | 0.96265 | 0.9206 | 0.87874 | 0.86516 | 0.75386 | 0.75583 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.71038 | 0.70944 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66638 | 0.66592 | 0.61181 | 0.61199 | 0.61872 | 0.61893 | 0.62606 | 0.6263
|  | B | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.9206 | 0.96265 | 1.2685 | 0.96265 | 0.96305 | 0.9208 | 0.73413 | 0.73555 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69608 | 0.69534 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65626 | 0.65587 | 0.60526 | 0.60543 | 0.61181 | 0.61199 | 0.61872 | 0.61893
|  | B | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.96265 | 0.9206 | 0.96265 | 1.2685 | 0.9208 | 0.96305 | 0.73555 | 0.73413 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69534 | 0.69608 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65587 | 0.65626 | 0.60543 | 0.60526 | 0.61199 | 0.61181 | 0.61893 | 0.61872
|  | C | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 1.2685 | 0.96265 | 0.71717 | 0.71824 | 0.73562 | 0.73419 | 0.7559 | 0.75393 | 0.66123 | 0.66081 | 0.67129 | 0.6718 | 0.68333 | 0.68273 | 0.62991 | 0.63016 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61183 | 0.61202
|  | C | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 0.96265 | 1.2685 | 0.71824 | 0.71717 | 0.73419 | 0.73562 | 0.75393 | 0.7559 | 0.66081 | 0.66123 | 0.6718 | 0.67129 | 0.68273 | 0.68333 | 0.63016 | 0.62991 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61202 | 0.61183
Circuit No. 6 |  | A | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66077 | 0.66119 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 0.71717 | 0.71824 | 1.2685 | 0.96265 | 0.9206 | 0.96265 | 0.86501 | 0.87854 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.84253 | 0.85155 | 0.71043 | 0.70949 | 0.72664 | 0.72542 | 0.7437 | 0.74537 | 0.65626 | 0.65587 | 0.66638 | 0.66592 | 0.67743 | 0.67688
|  | A | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66119 | 0.66077 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.71824 | 0.71717 | 0.96265 | 1.2685 | 0.96265 | 0.9206 | 0.87854 | 0.86501 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.85155 | 0.84253 | 0.70949 | 0.71043 | 0.72542 | 0.72664 | 0.74537 | 0.7437 | 0.65587 | 0.65626 | 0.66592 | 0.66638 | 0.67688 | 0.67743
|  | B | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.73562 | 0.73419 | 0.9206 | 0.96265 | 1.2685 | 0.96265 | 0.96265 | 0.9206 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.8107 | 0.80593 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.72664 | 0.72542 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66592 | 0.66638
|  | B | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.73419 | 0.73562 | 0.96265 | 0.9206 | 0.96265 | 1.2685 | 0.9206 | 0.96265 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.80593 | 0.8107 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.72542 | 0.72664 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66638 | 0.66592
|  | C | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.7559 | 0.75393 | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 1.2685 | 0.96265 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.78019 | 0.77726 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.71043 | 0.70949 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65587 | 0.65626
|  | C | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.75393 | 0.7559 | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 0.96265 | 1.2685 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.77726 | 0.78019 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.70949 | 0.71043 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65626 | 0.65587
Circuit No. 3 |  | A | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.62257 | 0.62235 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66123 | 0.66081 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73562 | 0.73419 | 1.2685 | 0.96265 | 0.9206 | 0.96265 | 0.87874 | 0.86516 | 0.80593 | 0.8107 | 0.84253 | 0.85155 | 0.91358 | 0.89123 | 0.70944 | 0.71038 | 0.72536 | 0.72659 | 0.74364 | 0.7453
|  | A | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.62235 | 0.62257 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66081 | 0.66123 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73419 | 0.73562 | 0.96265 | 1.2685 | 0.96265 | 0.9206 | 0.86516 | 0.87874 | 0.8107 | 0.80593 | 0.85155 | 0.84253 | 0.89123 | 0.91358 | 0.71038 | 0.70944 | 0.72659 | 0.72536 | 0.7453 | 0.74364
|  | B | 0.64661 | 0.64694 | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67129 | 0.6718 | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.75393 | 0.7559 | 0.9206 | 0.96265 | 1.2685 | 0.96265 | 0.9208 | 0.96305 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.84253 | 0.85155 | 0.69608 | 0.69534 | 0.71038 | 0.70944 | 0.72659 | 0.72536
|  | B | 0.64694 | 0.64661 | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.6718 | 0.67129 | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.7559 | 0.75393 | 0.96265 | 0.9206 | 0.96265 | 1.2685 | 0.96305 | 0.9208 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.85155 | 0.84253 | 0.69534 | 0.69608 | 0.70944 | 0.71038 | 0.72536 | 0.72659
|  | C | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68333 | 0.68273 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 1.2685 | 0.96265 | 0.75393 | 0.7559 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.70949 | 0.71043
|  | C | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68273 | 0.68333 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 0.96265 | 1.2685 | 0.7559 | 0.75393 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.71043 | 0.70949
Circuit No. 5 |  | A | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.59907 | 0.59922 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.62991 | 0.63016 | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68273 | 0.68333 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.75393 | 0.7559 | 1.2685 | 0.96265 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.85155 | 0.84253
|  | A | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.59922 | 0.59907 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.63016 | 0.62991 | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68333 | 0.68273 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.7559 | 0.75393 | 0.96265 | 1.2685 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.84253 | 0.85155
|  | B | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63797 | 0.63826 | 0.72664 | 0.72542 | 0.70949 | 0.71043 | 0.69538 | 0.69612 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77735 | 0.78028 | 0.96265 | 0.9206 | 1.2685 | 0.96265 | 0.9206 | 0.96265 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.8107 | 0.80593
|  | B | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63826 | 0.63797 | 0.72542 | 0.72664 | 0.71043 | 0.70949 | 0.69612 | 0.69538 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78028 | 0.77735 | 0.9206 | 0.96265 | 0.96265 | 1.2685 | 0.96265 | 0.9206 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.80593 | 0.8107
|  | C | 0.62632 | 0.62608 | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64694 | 0.64661 | 0.7437 | 0.74537 | 0.72664 | 0.72542 | 0.71043 | 0.70949 | 0.91358 | 0.89123 | 0.84253 | 0.85155 | 0.81081 | 0.80604 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 1.2685 | 0.96265 | 0.73413 | 0.73555 | 0.75386 | 0.75583 | 0.77726 | 0.78019
|  | C | 0.62608 | 0.62632 | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64661 | 0.64694 | 0.74537 | 0.7437 | 0.72542 | 0.72664 | 0.70949 | 0.71043 | 0.89123 | 0.91358 | 0.85155 | 0.84253 | 0.80604 | 0.81081 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 0.96265 | 1.2685 | 0.73555 | 0.73413 | 0.75583 | 0.75386 | 0.78019 | 0.77726
Circuit No. 2 |  | A | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.57449 | 0.57459 | 0.61199 | 0.61181 | 0.60526 | 0.60543 | 0.59907 | 0.59922 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63795 | 0.63823 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68273 | 0.68333 | 0.78019 | 0.77726 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 1.2685 | 0.96265 | 0.96265 | 0.9206 | 0.87854 | 0.86501
|  | A | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.57459 | 0.57449 | 0.61181 | 0.61199 | 0.60543 | 0.60526 | 0.59922 | 0.59907 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63823 | 0.63795 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68333 | 0.68273 | 0.77726 | 0.78019 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.96265 | 1.2685 | 0.9206 | 0.96265 | 0.86501 | 0.87854
|  | B | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.61893 | 0.61872 | 0.61181 | 0.61199 | 0.60528 | 0.60545 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64658 | 0.64691 | 0.72536 | 0.72659 | 0.71038 | 0.70944 | 0.69538 | 0.69612 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.96265 | 0.9206 | 1.2685 | 0.96265 | 0.96265 | 0.9206
|  | B | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.61872 | 0.61893 | 0.61199 | 0.61181 | 0.60545 | 0.60528 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64691 | 0.64658 | 0.72659 | 0.72536 | 0.70944 | 0.71038 | 0.69612 | 0.69538 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.9206 | 0.96265 | 0.96265 | 1.2685 | 0.9206 | 0.96265
|  | C | 0.59609 | 0.59623 | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.6263 | 0.62606 | 0.61872 | 0.61893 | 0.61183 | 0.61202 | 0.67743 | 0.67688 | 0.66592 | 0.66638 | 0.65587 | 0.65626 | 0.74364 | 0.7453 | 0.72659 | 0.72536 | 0.70949 | 0.71043 | 0.85155 | 0.84253 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 1.2685 | 0.96265
|  | C | 0.59623 | 0.59609 | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.62606 | 0.6263 | 0.61893 | 0.61872 | 0.61202 | 0.61183 | 0.67688 | 0.67743 | 0.66638 | 0.66592 | 0.65626 | 0.65587 | 0.7453 | 0.74364 | 0.72536 | 0.72659 | 0.71043 | 0.70949 | 0.84253 | 0.85155 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 0.96265 | 1.2685
R Phase [Ω/mile]
|  | Circuit No. 1 | [5 empty] | Circuit No. 2 | [5 empty] | Circuit No. 3 | [5 empty] | Circuit No. 4 | [5 empty] | Circuit No. 5 | [5 empty] | Circuit No. 6
|  | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C
Circuit No. 1 | A | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| A | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 2 | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11497 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 3 | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 4 | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 5 | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 6 | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.11517
X Phase [Ω/mile]
|  | Circuit No. 1 | [5 empty] | Circuit No. 2 | [5 empty] | Circuit No. 3 | [5 empty] | Circuit No. 4 | [5 empty] | Circuit No. 5 | [5 empty] | Circuit No. 6
|  | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C
Circuit No. 1 | A | 1.2685 | 0.96265 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.85155 | 0.84253 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.65626 | 0.65587 | 0.61183 | 0.61202 | 0.61875 | 0.61896 | 0.62632 | 0.62608 | 0.58481 | 0.58493 | 0.59032 | 0.59045 | 0.59609 | 0.59623
| A | 0.96265 | 1.2685 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.84253 | 0.85155 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.65587 | 0.65626 | 0.61202 | 0.61183 | 0.61896 | 0.61875 | 0.62608 | 0.62632 | 0.58493 | 0.58481 | 0.59045 | 0.59032 | 0.59623 | 0.59609
| B | 0.9206 | 0.96265 | 1.2685 | 0.96265 | 0.9206 | 0.96265 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.80593 | 0.8107 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.62991 | 0.63016 | 0.63826 | 0.63797 | 0.64658 | 0.64691 | 0.60545 | 0.60528 | 0.61202 | 0.61183 | 0.61875 | 0.61896 | 0.57965 | 0.57954 | 0.58493 | 0.58481 | 0.59045 | 0.59032
| B | 0.96265 | 0.9206 | 0.96265 | 1.2685 | 0.96265 | 0.9206 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.8107 | 0.80593 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.63016 | 0.62991 | 0.63797 | 0.63826 | 0.64691 | 0.64658 | 0.60528 | 0.60545 | 0.61183 | 0.61202 | 0.61896 | 0.61875 | 0.57954 | 0.57965 | 0.58481 | 0.58493 | 0.59032 | 0.59045
| C | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 1.2685 | 0.96265 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.78019 | 0.77726 | 0.66077 | 0.66119 | 0.67176 | 0.67126 | 0.68333 | 0.68273 | 0.62257 | 0.62235 | 0.62991 | 0.63016 | 0.63823 | 0.63795 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61202 | 0.61183 | 0.57449 | 0.57459 | 0.57954 | 0.57965 | 0.58481 | 0.58493
| C | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 0.96265 | 1.2685 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.77726 | 0.78019 | 0.66119 | 0.66077 | 0.67126 | 0.67176 | 0.68273 | 0.68333 | 0.62235 | 0.62257 | 0.63016 | 0.62991 | 0.63795 | 0.63823 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61183 | 0.61202 | 0.57459 | 0.57449 | 0.57965 | 0.57954 | 0.58493 | 0.58481
Circuit No. 2 | A | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73419 | 0.73562 | 1.2685 | 0.96265 | 0.9206 | 0.96265 | 0.86516 | 0.87874 | 0.75583 | 0.75386 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.68273 | 0.68333 | 0.69612 | 0.69538 | 0.70944 | 0.71038 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66592 | 0.66638 | 0.61199 | 0.61181 | 0.61893 | 0.61872 | 0.6263 | 0.62606
| A | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73562 | 0.73419 | 0.96265 | 1.2685 | 0.96265 | 0.9206 | 0.87874 | 0.86516 | 0.75386 | 0.75583 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.68333 | 0.68273 | 0.69538 | 0.69612 | 0.71038 | 0.70944 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66638 | 0.66592 | 0.61181 | 0.61199 | 0.61872 | 0.61893 | 0.62606 | 0.6263
| B | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.9206 | 0.96265 | 1.2685 | 0.96265 | 0.96305 | 0.9208 | 0.73413 | 0.73555 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.67176 | 0.67126 | 0.68273 | 0.68333 | 0.69608 | 0.69534 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65626 | 0.65587 | 0.60526 | 0.60543 | 0.61181 | 0.61199 | 0.61872 | 0.61893
| B | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.96265 | 0.9206 | 0.96265 | 1.2685 | 0.9208 | 0.96305 | 0.73555 | 0.73413 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.67126 | 0.67176 | 0.68333 | 0.68273 | 0.69534 | 0.69608 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65587 | 0.65626 | 0.60543 | 0.60526 | 0.61199 | 0.61181 | 0.61893 | 0.61872
| C | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 1.2685 | 0.96265 | 0.71717 | 0.71824 | 0.73562 | 0.73419 | 0.7559 | 0.75393 | 0.66123 | 0.66081 | 0.67129 | 0.6718 | 0.68333 | 0.68273 | 0.62991 | 0.63016 | 0.63797 | 0.63826 | 0.64694 | 0.64661 | 0.59907 | 0.59922 | 0.60528 | 0.60545 | 0.61183 | 0.61202
| C | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 0.96265 | 1.2685 | 0.71824 | 0.71717 | 0.73419 | 0.73562 | 0.75393 | 0.7559 | 0.66081 | 0.66123 | 0.6718 | 0.67129 | 0.68273 | 0.68333 | 0.63016 | 0.62991 | 0.63826 | 0.63797 | 0.64661 | 0.64694 | 0.59922 | 0.59907 | 0.60545 | 0.60528 | 0.61202 | 0.61183
Circuit No. 3 | A | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66077 | 0.66119 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 0.71717 | 0.71824 | 1.2685 | 0.96265 | 0.9206 | 0.96265 | 0.86501 | 0.87854 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.84253 | 0.85155 | 0.71043 | 0.70949 | 0.72664 | 0.72542 | 0.7437 | 0.74537 | 0.65626 | 0.65587 | 0.66638 | 0.66592 | 0.67743 | 0.67688
| A | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66119 | 0.66077 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.71824 | 0.71717 | 0.96265 | 1.2685 | 0.96265 | 0.9206 | 0.87854 | 0.86501 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.85155 | 0.84253 | 0.70949 | 0.71043 | 0.72542 | 0.72664 | 0.74537 | 0.7437 | 0.65587 | 0.65626 | 0.66592 | 0.66638 | 0.67688 | 0.67743
| B | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.73562 | 0.73419 | 0.9206 | 0.96265 | 1.2685 | 0.96265 | 0.96265 | 0.9206 | 0.7559 | 0.75393 | 0.77735 | 0.78028 | 0.8107 | 0.80593 | 0.69538 | 0.69612 | 0.70949 | 0.71043 | 0.72664 | 0.72542 | 0.64658 | 0.64691 | 0.65587 | 0.65626 | 0.66592 | 0.66638
| B | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.73419 | 0.73562 | 0.96265 | 0.9206 | 0.96265 | 1.2685 | 0.9206 | 0.96265 | 0.75393 | 0.7559 | 0.78028 | 0.77735 | 0.80593 | 0.8107 | 0.69612 | 0.69538 | 0.71043 | 0.70949 | 0.72542 | 0.72664 | 0.64691 | 0.64658 | 0.65626 | 0.65587 | 0.66638 | 0.66592
| C | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.7559 | 0.75393 | 0.86501 | 0.87854 | 0.96265 | 0.9206 | 1.2685 | 0.96265 | 0.73562 | 0.73419 | 0.75393 | 0.7559 | 0.78019 | 0.77726 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.71043 | 0.70949 | 0.63795 | 0.63823 | 0.64658 | 0.64691 | 0.65587 | 0.65626
| C | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.75393 | 0.7559 | 0.87854 | 0.86501 | 0.9206 | 0.96265 | 0.96265 | 1.2685 | 0.73419 | 0.73562 | 0.7559 | 0.75393 | 0.77726 | 0.78019 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.70949 | 0.71043 | 0.63823 | 0.63795 | 0.64691 | 0.64658 | 0.65626 | 0.65587
Circuit No. 4 | A | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.62257 | 0.62235 | 0.68273 | 0.68333 | 0.67176 | 0.67126 | 0.66123 | 0.66081 | 0.77735 | 0.78028 | 0.7559 | 0.75393 | 0.73562 | 0.73419 | 1.2685 | 0.96265 | 0.9206 | 0.96265 | 0.87874 | 0.86516 | 0.80593 | 0.8107 | 0.84253 | 0.85155 | 0.91358 | 0.89123 | 0.70944 | 0.71038 | 0.72536 | 0.72659 | 0.74364 | 0.7453
| A | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.62235 | 0.62257 | 0.68333 | 0.68273 | 0.67126 | 0.67176 | 0.66081 | 0.66123 | 0.78028 | 0.77735 | 0.75393 | 0.7559 | 0.73419 | 0.73562 | 0.96265 | 1.2685 | 0.96265 | 0.9206 | 0.86516 | 0.87874 | 0.8107 | 0.80593 | 0.85155 | 0.84253 | 0.89123 | 0.91358 | 0.71038 | 0.70944 | 0.72659 | 0.72536 | 0.7453 | 0.74364
| B | 0.64661 | 0.64694 | 0.63826 | 0.63797 | 0.62991 | 0.63016 | 0.69612 | 0.69538 | 0.68273 | 0.68333 | 0.67129 | 0.6718 | 0.81081 | 0.80604 | 0.77735 | 0.78028 | 0.75393 | 0.7559 | 0.9206 | 0.96265 | 1.2685 | 0.96265 | 0.9208 | 0.96305 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.84253 | 0.85155 | 0.69608 | 0.69534 | 0.71038 | 0.70944 | 0.72659 | 0.72536
| B | 0.64694 | 0.64661 | 0.63797 | 0.63826 | 0.63016 | 0.62991 | 0.69538 | 0.69612 | 0.68333 | 0.68273 | 0.6718 | 0.67129 | 0.80604 | 0.81081 | 0.78028 | 0.77735 | 0.7559 | 0.75393 | 0.96265 | 0.9206 | 0.96265 | 1.2685 | 0.96305 | 0.9208 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.85155 | 0.84253 | 0.69534 | 0.69608 | 0.70944 | 0.71038 | 0.72536 | 0.72659
| C | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68333 | 0.68273 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.87874 | 0.86516 | 0.9208 | 0.96305 | 1.2685 | 0.96265 | 0.75393 | 0.7559 | 0.77735 | 0.78028 | 0.81081 | 0.80604 | 0.68273 | 0.68333 | 0.69538 | 0.69612 | 0.70949 | 0.71043
| C | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68273 | 0.68333 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.86516 | 0.87874 | 0.96305 | 0.9208 | 0.96265 | 1.2685 | 0.7559 | 0.75393 | 0.78028 | 0.77735 | 0.80604 | 0.81081 | 0.68333 | 0.68273 | 0.69612 | 0.69538 | 0.71043 | 0.70949
Circuit No. 5 | A | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.59907 | 0.59922 | 0.64691 | 0.64658 | 0.63795 | 0.63823 | 0.62991 | 0.63016 | 0.71043 | 0.70949 | 0.69538 | 0.69612 | 0.68273 | 0.68333 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.75393 | 0.7559 | 1.2685 | 0.96265 | 0.96265 | 0.9206 | 0.86501 | 0.87854 | 0.78019 | 0.77726 | 0.8107 | 0.80593 | 0.85155 | 0.84253
| A | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.59922 | 0.59907 | 0.64658 | 0.64691 | 0.63823 | 0.63795 | 0.63016 | 0.62991 | 0.70949 | 0.71043 | 0.69612 | 0.69538 | 0.68333 | 0.68273 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.7559 | 0.75393 | 0.96265 | 1.2685 | 0.9206 | 0.96265 | 0.87854 | 0.86501 | 0.77726 | 0.78019 | 0.80593 | 0.8107 | 0.84253 | 0.85155
| B | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.60528 | 0.60545 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63797 | 0.63826 | 0.72664 | 0.72542 | 0.70949 | 0.71043 | 0.69538 | 0.69612 | 0.84253 | 0.85155 | 0.8107 | 0.80593 | 0.77735 | 0.78028 | 0.96265 | 0.9206 | 1.2685 | 0.96265 | 0.9206 | 0.96265 | 0.75583 | 0.75386 | 0.78019 | 0.77726 | 0.8107 | 0.80593
| B | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.60545 | 0.60528 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63826 | 0.63797 | 0.72542 | 0.72664 | 0.71043 | 0.70949 | 0.69612 | 0.69538 | 0.85155 | 0.84253 | 0.80593 | 0.8107 | 0.78028 | 0.77735 | 0.9206 | 0.96265 | 0.96265 | 1.2685 | 0.96265 | 0.9206 | 0.75386 | 0.75583 | 0.77726 | 0.78019 | 0.80593 | 0.8107
| C | 0.62632 | 0.62608 | 0.61875 | 0.61896 | 0.61202 | 0.61183 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64694 | 0.64661 | 0.7437 | 0.74537 | 0.72664 | 0.72542 | 0.71043 | 0.70949 | 0.91358 | 0.89123 | 0.84253 | 0.85155 | 0.81081 | 0.80604 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 1.2685 | 0.96265 | 0.73413 | 0.73555 | 0.75386 | 0.75583 | 0.77726 | 0.78019
| C | 0.62608 | 0.62632 | 0.61896 | 0.61875 | 0.61183 | 0.61202 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64661 | 0.64694 | 0.74537 | 0.7437 | 0.72542 | 0.72664 | 0.70949 | 0.71043 | 0.89123 | 0.91358 | 0.85155 | 0.84253 | 0.80604 | 0.81081 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 0.96265 | 1.2685 | 0.73555 | 0.73413 | 0.75583 | 0.75386 | 0.78019 | 0.77726
Circuit No. 6 | A | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.57449 | 0.57459 | 0.61199 | 0.61181 | 0.60526 | 0.60543 | 0.59907 | 0.59922 | 0.65626 | 0.65587 | 0.64658 | 0.64691 | 0.63795 | 0.63823 | 0.70944 | 0.71038 | 0.69608 | 0.69534 | 0.68273 | 0.68333 | 0.78019 | 0.77726 | 0.75583 | 0.75386 | 0.73413 | 0.73555 | 1.2685 | 0.96265 | 0.96265 | 0.9206 | 0.87854 | 0.86501
| A | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.57459 | 0.57449 | 0.61181 | 0.61199 | 0.60543 | 0.60526 | 0.59922 | 0.59907 | 0.65587 | 0.65626 | 0.64691 | 0.64658 | 0.63823 | 0.63795 | 0.71038 | 0.70944 | 0.69534 | 0.69608 | 0.68333 | 0.68273 | 0.77726 | 0.78019 | 0.75386 | 0.75583 | 0.73555 | 0.73413 | 0.96265 | 1.2685 | 0.9206 | 0.96265 | 0.86501 | 0.87854
| B | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.57954 | 0.57965 | 0.61893 | 0.61872 | 0.61181 | 0.61199 | 0.60528 | 0.60545 | 0.66638 | 0.66592 | 0.65587 | 0.65626 | 0.64658 | 0.64691 | 0.72536 | 0.72659 | 0.71038 | 0.70944 | 0.69538 | 0.69612 | 0.8107 | 0.80593 | 0.78019 | 0.77726 | 0.75386 | 0.75583 | 0.96265 | 0.9206 | 1.2685 | 0.96265 | 0.96265 | 0.9206
| B | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.57965 | 0.57954 | 0.61872 | 0.61893 | 0.61199 | 0.61181 | 0.60545 | 0.60528 | 0.66592 | 0.66638 | 0.65626 | 0.65587 | 0.64691 | 0.64658 | 0.72659 | 0.72536 | 0.70944 | 0.71038 | 0.69612 | 0.69538 | 0.80593 | 0.8107 | 0.77726 | 0.78019 | 0.75583 | 0.75386 | 0.9206 | 0.96265 | 0.96265 | 1.2685 | 0.9206 | 0.96265
| C | 0.59609 | 0.59623 | 0.59045 | 0.59032 | 0.58481 | 0.58493 | 0.6263 | 0.62606 | 0.61872 | 0.61893 | 0.61183 | 0.61202 | 0.67743 | 0.67688 | 0.66592 | 0.66638 | 0.65587 | 0.65626 | 0.74364 | 0.7453 | 0.72659 | 0.72536 | 0.70949 | 0.71043 | 0.85155 | 0.84253 | 0.8107 | 0.80593 | 0.77726 | 0.78019 | 0.87854 | 0.86501 | 0.96265 | 0.9206 | 1.2685 | 0.96265
| C | 0.59623 | 0.59609 | 0.59032 | 0.59045 | 0.58493 | 0.58481 | 0.62606 | 0.6263 | 0.61893 | 0.61872 | 0.61202 | 0.61183 | 0.67688 | 0.67743 | 0.66638 | 0.66592 | 0.65626 | 0.65587 | 0.7453 | 0.74364 | 0.72536 | 0.72659 | 0.71043 | 0.70949 | 0.84253 | 0.85155 | 0.80593 | 0.8107 | 0.78019 | 0.77726 | 0.86501 | 0.87854 | 0.9206 | 0.96265 | 0.96265 | 1.2685
R Circuit [Ω/mile]
|  | Circuit No. 1 |  |  | Circuit No. 2 |  |  | Circuit No. 3 |  |  | Circuit No. 4 |  |  | Circuit No. 5 |  |  | Circuit No. 6
|  | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C
Circuit No. 1 | A | 0.10523 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.10523 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| C | 0.095302 | 0.095302 | 0.10523 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 2 | A | 0.095302 | 0.095302 | 0.095302 | 0.10523 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.10523 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.10519 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 3 | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.10523 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.10523 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.10523 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 4 | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.10523 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.10523 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.10523 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
Circuit No. 5 | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.10523 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.10523 | 0.095302 | 0.095302 | 0.095302 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.10523 | 0.095302 | 0.095302 | 0.095302
Circuit No. 6 | A | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.10523 | 0.095302 | 0.095302
| B | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.10523 | 0.095302
| C | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.095302 | 0.10523
X Circuit [Ω/mile]
|  | Circuit No. 1 |  |  | Circuit No. 2 |  |  | Circuit No. 3 |  |  | Circuit No. 4 |  |  | Circuit No. 5 |  |  | Circuit No. 6
|  | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C
Circuit No. 1 | A | 1.1156 | 0.94162 | 0.87177 | 0.77881 | 0.80842 | 0.84704 | 0.68303 | 0.69575 | 0.70996 | 0.63812 | 0.64677 | 0.65606 | 0.61192 | 0.61885 | 0.6262 | 0.58487 | 0.59039 | 0.59616
| B | 0.94162 | 1.1156 | 0.94162 | 0.75491 | 0.77881 | 0.80831 | 0.67151 | 0.68303 | 0.69575 | 0.63004 | 0.63812 | 0.64674 | 0.60537 | 0.61192 | 0.61885 | 0.5796 | 0.58487 | 0.59039
| C | 0.87177 | 0.94162 | 1.1156 | 0.73491 | 0.75491 | 0.77873 | 0.66099 | 0.67151 | 0.68303 | 0.62246 | 0.63004 | 0.63809 | 0.59915 | 0.60537 | 0.61192 | 0.57454 | 0.5796 | 0.58487
Circuit No. 2 | A | 0.77881 | 0.75491 | 0.73491 | 1.1156 | 0.94162 | 0.87195 | 0.75484 | 0.77873 | 0.80831 | 0.68303 | 0.69575 | 0.70991 | 0.64674 | 0.65606 | 0.66615 | 0.6119 | 0.61883 | 0.62618
| B | 0.80842 | 0.77881 | 0.75491 | 0.94162 | 1.1156 | 0.94192 | 0.73484 | 0.75484 | 0.77873 | 0.67151 | 0.68303 | 0.69571 | 0.63809 | 0.64674 | 0.65606 | 0.60535 | 0.6119 | 0.61883
| C | 0.84704 | 0.80831 | 0.77873 | 0.87195 | 0.94192 | 1.1156 | 0.7177 | 0.73491 | 0.75491 | 0.66102 | 0.67154 | 0.68303 | 0.63004 | 0.63812 | 0.64677 | 0.59915 | 0.60537 | 0.61192
Circuit No. 3 | A | 0.68303 | 0.67151 | 0.66099 | 0.75484 | 0.73484 | 0.7177 | 1.1156 | 0.94162 | 0.87177 | 0.77881 | 0.80842 | 0.84704 | 0.70996 | 0.72603 | 0.74454 | 0.65606 | 0.66615 | 0.67715
| B | 0.69575 | 0.68303 | 0.67151 | 0.77873 | 0.75484 | 0.73491 | 0.94162 | 1.1156 | 0.94162 | 0.75491 | 0.77881 | 0.80831 | 0.69575 | 0.70996 | 0.72603 | 0.64674 | 0.65606 | 0.66615
| C | 0.70996 | 0.69575 | 0.68303 | 0.80831 | 0.77873 | 0.75491 | 0.87177 | 0.94162 | 1.1156 | 0.73491 | 0.75491 | 0.77873 | 0.68303 | 0.69575 | 0.70996 | 0.63809 | 0.64674 | 0.65606
Circuit No. 4 | A | 0.63812 | 0.63004 | 0.62246 | 0.68303 | 0.67151 | 0.66102 | 0.77881 | 0.75491 | 0.73491 | 1.1156 | 0.94162 | 0.87195 | 0.80831 | 0.84704 | 0.90241 | 0.70991 | 0.72598 | 0.74447
| B | 0.64677 | 0.63812 | 0.63004 | 0.69575 | 0.68303 | 0.67154 | 0.80842 | 0.77881 | 0.75491 | 0.94162 | 1.1156 | 0.94192 | 0.77873 | 0.80831 | 0.84704 | 0.69571 | 0.70991 | 0.72598
| C | 0.65606 | 0.64674 | 0.63809 | 0.70991 | 0.69571 | 0.68303 | 0.84704 | 0.80831 | 0.77873 | 0.87195 | 0.94192 | 1.1156 | 0.75491 | 0.77881 | 0.80842 | 0.68303 | 0.69575 | 0.70996
Circuit No. 5 | A | 0.61192 | 0.60537 | 0.59915 | 0.64674 | 0.63809 | 0.63004 | 0.70996 | 0.69575 | 0.68303 | 0.80831 | 0.77873 | 0.75491 | 1.1156 | 0.94162 | 0.87177 | 0.77873 | 0.80831 | 0.84704
| B | 0.61885 | 0.61192 | 0.60537 | 0.65606 | 0.64674 | 0.63812 | 0.72603 | 0.70996 | 0.69575 | 0.84704 | 0.80831 | 0.77881 | 0.94162 | 1.1156 | 0.94162 | 0.75484 | 0.77873 | 0.80831
| C | 0.6262 | 0.61885 | 0.61192 | 0.66615 | 0.65606 | 0.64677 | 0.74454 | 0.72603 | 0.70996 | 0.90241 | 0.84704 | 0.80842 | 0.87177 | 0.94162 | 1.1156 | 0.73484 | 0.75484 | 0.77873
Circuit No. 6 | A | 0.58487 | 0.5796 | 0.57454 | 0.6119 | 0.60535 | 0.59915 | 0.65606 | 0.64674 | 0.63809 | 0.70991 | 0.69571 | 0.68303 | 0.77873 | 0.75484 | 0.73484 | 1.1156 | 0.94162 | 0.87177
| B | 0.59039 | 0.58487 | 0.5796 | 0.61883 | 0.6119 | 0.60537 | 0.66615 | 0.65606 | 0.64674 | 0.72598 | 0.70991 | 0.69575 | 0.80831 | 0.77873 | 0.75484 | 0.94162 | 1.1156 | 0.94162
| C | 0.59616 | 0.59039 | 0.58487 | 0.62618 | 0.61883 | 0.61192 | 0.67715 | 0.66615 | 0.65606 | 0.74447 | 0.72598 | 0.70996 | 0.84704 | 0.80831 | 0.77873 | 0.87177 | 0.94162 | 1.1156
R Sequence [Ω/mile]
|  | Circuit No. 1 |  |  | Circuit No. 2 |  |  | Circuit No. 3 |  |  | Circuit No. 4 |  |  | Circuit No. 5 |  |  | Circuit No. 6
|  | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 2
Circuit No. 1 | 0 | 0.29584 | 0.020164 | -0.020164 | 0.28591 | -0.026537 | 0.026537 | 0.28591 | -0.011099 | 0.011099 | 0.28591 | -0.007496 | 0.007496 | 0.28591 | -0.006014 | 0.006014 | 0.28591 | -0.004782 | 0.004782
| 1 | -0.020164 | 0.009932 | -0.040328 | -0.021216 | -0.001509 | 0.005396 | -0.010036 | -0.00014 | 0.001062 | -0.007018 | -4.5e-05 | 0.000502 | -0.005688 | -2.4e-05 | 0.000326 | -0.004574 | -1.2e-05 | 0.000208
| 2 | 0.020164 | 0.040328 | 0.009932 | 0.021216 | -0.005396 | 0.001509 | 0.010036 | -0.001062 | 0.00014 | 0.007018 | -0.000502 | 4.5e-05 | 0.005688 | -0.000326 | 2.4e-05 | 0.004574 | -0.000208 | 1.2e-05
Circuit No. 2 | 0 | 0.28591 | 0.021216 | -0.021216 | 0.29582 | 0.02012 | -0.020104 | 0.28591 | -0.021212 | 0.021212 | 0.28591 | -0.011062 | 0.011062 | 0.28591 | -0.008101 | 0.008101 | 0.28591 | -0.006013 | 0.006013
| 1 | 0.026537 | 0.001509 | 0.005396 | -0.020104 | 0.009916 | -0.040217 | -0.017577 | -0.00084 | 0.003573 | -0.010004 | -0.00014 | 0.001058 | -0.007496 | -5.8e-05 | 0.000579 | -0.005669 | -2.4e-05 | 0.000325
| 2 | -0.026537 | -0.005396 | -0.001509 | 0.02012 | 0.040232 | 0.009916 | 0.017577 | -0.003573 | 0.00084 | 0.010004 | -0.001058 | 0.00014 | 0.007496 | -0.000579 | 5.8e-05 | 0.005669 | -0.000325 | 2.4e-05
Circuit No. 3 | 0 | 0.28591 | 0.010036 | -0.010036 | 0.28591 | 0.017577 | -0.017577 | 0.29584 | 0.020164 | -0.020164 | 0.28591 | -0.026537 | 0.026537 | 0.28591 | -0.014083 | 0.014083 | 0.28591 | -0.008778 | 0.008778
| 1 | 0.011099 | 0.00014 | 0.001062 | 0.021212 | 0.00084 | 0.003573 | -0.020164 | 0.009932 | -0.040328 | -0.021216 | -0.001509 | 0.005396 | -0.012414 | -0.000274 | 0.001669 | -0.0081 | -7.2e-05 | 0.000678
| 2 | -0.011099 | -0.001062 | -0.00014 | -0.021212 | -0.003573 | -0.00084 | 0.020164 | 0.040328 | 0.009932 | 0.021216 | -0.005396 | 0.001509 | 0.012414 | -0.001669 | 0.000274 | 0.0081 | -0.000678 | 7.2e-05
Circuit No. 4 | 0 | 0.28591 | 0.007018 | -0.007018 | 0.28591 | 0.010004 | -0.010004 | 0.28591 | 0.021216 | -0.021216 | 0.29584 | 0.020112 | -0.020112 | 0.28591 | -0.035711 | 0.035711 | 0.28591 | -0.014078 | 0.014078
| 1 | 0.007496 | 4.5e-05 | 0.000502 | 0.011062 | 0.00014 | 0.001058 | 0.026537 | 0.001509 | 0.005396 | -0.020112 | 0.009932 | -0.040224 | -0.026537 | -0.003162 | 0.009079 | -0.01237 | -0.000275 | 0.001665
| 2 | -0.007496 | -0.000502 | -4.5e-05 | -0.011062 | -0.001058 | -0.00014 | -0.026537 | -0.005396 | -0.001509 | 0.020112 | 0.040224 | 0.009932 | 0.026537 | -0.009079 | 0.003162 | 0.01237 | -0.001665 | 0.000275
Circuit No. 5 | 0 | 0.28591 | 0.005688 | -0.005688 | 0.28591 | 0.007496 | -0.007496 | 0.28591 | 0.012414 | -0.012414 | 0.28591 | 0.026537 | -0.026537 | 0.29584 | 0.020164 | -0.020164 | 0.28591 | -0.026615 | 0.026615
| 1 | 0.006014 | 2.4e-05 | 0.000326 | 0.008101 | 5.8e-05 | 0.000579 | 0.014083 | 0.000274 | 0.001669 | 0.035711 | 0.003162 | 0.009079 | -0.020164 | 0.009932 | -0.040328 | -0.021209 | -0.001517 | 0.005406
| 2 | -0.006014 | -0.000326 | -2.4e-05 | -0.008101 | -0.000579 | -5.8e-05 | -0.014083 | -0.001669 | -0.000274 | -0.035711 | -0.009079 | -0.003162 | 0.020164 | 0.040328 | 0.009932 | 0.021209 | -0.005406 | 0.001517
Circuit No. 6 | 0 | 0.28591 | 0.004574 | -0.004574 | 0.28591 | 0.005669 | -0.005669 | 0.28591 | 0.0081 | -0.0081 | 0.28591 | 0.01237 | -0.01237 | 0.28591 | 0.021209 | -0.021209 | 0.29584 | 0.020164 | -0.020164
| 1 | 0.004782 | 1.2e-05 | 0.000208 | 0.006013 | 2.4e-05 | 0.000325 | 0.008778 | 7.2e-05 | 0.000678 | 0.014078 | 0.000275 | 0.001665 | 0.026615 | 0.001517 | 0.005406 | -0.020164 | 0.009932 | -0.040328
| 2 | -0.004782 | -0.000208 | -1.2e-05 | -0.006013 | -0.000325 | -2.4e-05 | -0.008778 | -0.000678 | -7.2e-05 | -0.014078 | -0.001665 | -0.000275 | -0.026615 | -0.005406 | -0.001517 | 0.020164 | 0.040328 | 0.009932
X Sequence [Ω/mile]
|  | Circuit No. 1 |  |  | Circuit No. 2 |  |  | Circuit No. 3 |  |  | Circuit No. 4 |  |  | Circuit No. 5 |  |  | Circuit No. 6
|  | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 2
Circuit No. 1 | 0 | 2.9522 | -0.011642 | -0.011642 | 2.3483 | -0.039827 | -0.039827 | 2.0515 | -0.017997 | -0.017997 | 1.9155 | -0.012432 | -0.012432 | 1.8365 | -0.010041 | -0.010041 | 1.7551 | -0.008043 | -0.008043
| 1 | -0.011642 | 0.19721 | 0.023283 | 0.042994 | -0.005969 | -0.003123 | 0.01861 | -0.001215 | -0.000613 | 0.012736 | -0.000577 | -0.00029 | 0.010229 | -0.000375 | -0.000188 | 0.008163 | -0.00024 | -0.00012
| 2 | -0.011642 | 0.023283 | 0.19721 | 0.042994 | -0.003123 | -0.005969 | 0.01861 | -0.000613 | -0.001215 | 0.012736 | -0.00029 | -0.000577 | 0.010229 | -0.000188 | -0.000375 | 0.008163 | -0.00012 | -0.00024
Circuit No. 2 | 0 | 2.3483 | 0.042994 | 0.042994 | 2.9526 | -0.011725 | -0.011698 | 2.2726 | -0.032607 | -0.032607 | 2.0515 | -0.017977 | -0.017977 | 1.9416 | -0.013361 | -0.013361 | 1.8365 | -0.010039 | -0.010039
| 1 | -0.039827 | -0.005969 | -0.003123 | -0.011698 | 0.19705 | 0.023409 | 0.034638 | -0.004002 | -0.002066 | 0.01859 | -0.001211 | -0.000613 | 0.013681 | -0.000666 | -0.000335 | 0.010216 | -0.000374 | -0.000188
| 2 | -0.039827 | -0.003123 | -0.005969 | -0.011725 | 0.023436 | 0.19705 | 0.034638 | -0.002066 | -0.004002 | 0.01859 | -0.000613 | -0.001211 | 0.013681 | -0.000335 | -0.000666 | 0.010216 | -0.000188 | -0.000374
Circuit No. 3 | 0 | 2.0515 | 0.01861 | 0.01861 | 2.2726 | 0.034638 | 0.034638 | 2.9522 | -0.011642 | -0.011642 | 2.3483 | -0.039827 | -0.039827 | 2.1337 | -0.022465 | -0.022465 | 1.9697 | -0.014421 | -0.014421
| 1 | -0.017997 | -0.001215 | -0.000613 | -0.032607 | -0.004002 | -0.002066 | -0.011642 | 0.19721 | 0.023283 | 0.042994 | -0.005969 | -0.003123 | 0.023428 | -0.001898 | -0.000964 | 0.014813 | -0.000778 | -0.000391
| 2 | -0.017997 | -0.000613 | -0.001215 | -0.032607 | -0.002066 | -0.004002 | -0.011642 | 0.023283 | 0.19721 | 0.042994 | -0.003123 | -0.005969 | 0.023428 | -0.000964 | -0.001898 | 0.014813 | -0.000391 | -0.000778
Circuit No. 4 | 0 | 1.9155 | 0.012736 | 0.012736 | 2.0515 | 0.01859 | 0.01859 | 2.3483 | 0.042994 | 0.042994 | 2.9526 | -0.011711 | -0.011711 | 2.4447 | -0.051355 | -0.051355 | 2.1336 | -0.022458 | -0.022458
| 1 | -0.012432 | -0.000577 | -0.00029 | -0.017977 | -0.001211 | -0.000613 | -0.039827 | -0.005969 | -0.003123 | -0.011711 | 0.19705 | 0.023423 | 0.056549 | -0.009807 | -0.005249 | 0.023396 | -0.001894 | -0.000963
| 2 | -0.012432 | -0.00029 | -0.000577 | -0.017977 | -0.000613 | -0.001211 | -0.039827 | -0.003123 | -0.005969 | -0.011711 | 0.023423 | 0.19705 | 0.056549 | -0.005249 | -0.009807 | 0.023396 | -0.000963 | -0.001894
Circuit No. 5 | 0 | 1.8365 | 0.010229 | 0.010229 | 1.9416 | 0.013681 | 0.013681 | 2.1337 | 0.023428 | 0.023428 | 2.4447 | 0.056549 | 0.056549 | 2.9522 | -0.011642 | -0.011642 | 2.3481 | -0.039856 | -0.039856
| 1 | -0.010041 | -0.000375 | -0.000188 | -0.013361 | -0.000666 | -0.000335 | -0.022465 | -0.001898 | -0.000964 | -0.051355 | -0.009807 | -0.005249 | -0.011642 | 0.19721 | 0.023283 | 0.042977 | -0.005974 | -0.003121
| 2 | -0.010041 | -0.000188 | -0.000375 | -0.013361 | -0.000335 | -0.000666 | -0.022465 | -0.000964 | -0.001898 | -0.051355 | -0.005249 | -0.009807 | -0.011642 | 0.023283 | 0.19721 | 0.042977 | -0.003121 | -0.005974
Circuit No. 6 | 0 | 1.7551 | 0.008163 | 0.008163 | 1.8365 | 0.010216 | 0.010216 | 1.9697 | 0.014813 | 0.014813 | 2.1336 | 0.023396 | 0.023396 | 2.3481 | 0.042977 | 0.042977 | 2.9522 | -0.011642 | -0.011642
| 1 | -0.008043 | -0.00024 | -0.00012 | -0.010039 | -0.000374 | -0.000188 | -0.014421 | -0.000778 | -0.000391 | -0.022458 | -0.001894 | -0.000963 | -0.039856 | -0.005974 | -0.003121 | -0.011642 | 0.19721 | 0.023283
| 2 | -0.008043 | -0.00012 | -0.00024 | -0.010039 | -0.000188 | -0.000374 | -0.014421 | -0.000391 | -0.000778 | -0.022458 | -0.000963 | -0.001894 | -0.039856 | -0.003121 | -0.005974 | -0.011642 | 0.023283 | 0.19721
R Sequence/R1
|  | Circuit No. 1 |  |  | Circuit No. 2 |  |  | Circuit No. 3 |  |  | Circuit No. 4 |  |  | Circuit No. 5 |  |  | Circuit No. 6
|  | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 2
Circuit No. 1 | 0 | 29.7867 | 2.0302 | 2.0302 | 28.7867 | 2.672 | 2.672 | 28.7867 | 1.1175 | 1.1175 | 28.7867 | 0.75476 | 0.75476 | 28.7867 | 0.60555 | 0.60555 | 28.7867 | 0.48151 | 0.48151
| 1 | 2.0302 | 1 | 4.0605 | 2.1362 | 0.15193 | 0.54332 | 1.0105 | 0.014127 | 0.10697 | 0.70663 | 0.00457 | 0.050514 | 0.57275 | 0.002424 | 0.032804 | 0.46054 | 0.001241 | 0.020969
| 2 | 2.0302 | 4.0605 | 1 | 2.1362 | 0.54332 | 0.15193 | 1.0105 | 0.10697 | 0.014127 | 0.70663 | 0.050514 | 0.00457 | 0.57275 | 0.032804 | 0.002424 | 0.46054 | 0.020969 | 0.001241
Circuit No. 2 | 0 | 28.7867 | 2.1362 | 2.1362 | 29.7851 | 2.0258 | 2.0242 | 28.7867 | 2.1357 | 2.1357 | 28.7867 | 1.1137 | 1.1137 | 28.7867 | 0.81565 | 0.81565 | 28.7867 | 0.60547 | 0.60547
| 1 | 2.672 | 0.15193 | 0.54332 | 2.0242 | 0.9984 | 4.0493 | 1.7698 | 0.084536 | 0.35973 | 1.0072 | 0.014056 | 0.1065 | 0.75476 | 0.005794 | 0.05833 | 0.57082 | 0.002453 | 0.032728
| 2 | 2.672 | 0.54332 | 0.15193 | 2.0258 | 4.0509 | 0.9984 | 1.7698 | 0.35973 | 0.084536 | 1.0072 | 0.1065 | 0.014056 | 0.75476 | 0.05833 | 0.005794 | 0.57082 | 0.032728 | 0.002453
Circuit No. 3 | 0 | 28.7867 | 1.0105 | 1.0105 | 28.7867 | 1.7698 | 1.7698 | 29.7867 | 2.0302 | 2.0302 | 28.7867 | 2.672 | 2.672 | 28.7867 | 1.4179 | 1.4179 | 28.7867 | 0.88382 | 0.88382
| 1 | 1.1175 | 0.014127 | 0.10697 | 2.1357 | 0.084536 | 0.35973 | 2.0302 | 1 | 4.0605 | 2.1362 | 0.15193 | 0.54332 | 1.2499 | 0.02758 | 0.16806 | 0.81559 | 0.007235 | 0.068231
| 2 | 1.1175 | 0.10697 | 0.014127 | 2.1357 | 0.35973 | 0.084536 | 2.0302 | 4.0605 | 1 | 2.1362 | 0.54332 | 0.15193 | 1.2499 | 0.16806 | 0.02758 | 0.81559 | 0.068231 | 0.007235
Circuit No. 4 | 0 | 28.7867 | 0.70663 | 0.70663 | 28.7867 | 1.0072 | 1.0072 | 28.7867 | 2.1362 | 2.1362 | 29.7867 | 2.025 | 2.025 | 28.7867 | 3.5956 | 3.5956 | 28.7867 | 1.4175 | 1.4175
| 1 | 0.75476 | 0.00457 | 0.050514 | 1.1137 | 0.014056 | 0.1065 | 2.672 | 0.15193 | 0.54332 | 2.025 | 1 | 4.0501 | 2.672 | 0.31835 | 0.91411 | 1.2455 | 0.027673 | 0.16763
| 2 | 0.75476 | 0.050514 | 0.00457 | 1.1137 | 0.1065 | 0.014056 | 2.672 | 0.54332 | 0.15193 | 2.025 | 4.0501 | 1 | 2.672 | 0.91411 | 0.31835 | 1.2455 | 0.16763 | 0.027673
Circuit No. 5 | 0 | 28.7867 | 0.57275 | 0.57275 | 28.7867 | 0.75476 | 0.75476 | 28.7867 | 1.2499 | 1.2499 | 28.7867 | 2.672 | 2.672 | 29.7867 | 2.0302 | 2.0302 | 28.7867 | 2.6797 | 2.6797
| 1 | 0.60555 | 0.002424 | 0.032804 | 0.81565 | 0.005794 | 0.05833 | 1.4179 | 0.02758 | 0.16806 | 3.5956 | 0.31835 | 0.91411 | 2.0302 | 1 | 4.0605 | 2.1354 | 0.15273 | 0.5443
| 2 | 0.60555 | 0.032804 | 0.002424 | 0.81565 | 0.05833 | 0.005794 | 1.4179 | 0.16806 | 0.02758 | 3.5956 | 0.91411 | 0.31835 | 2.0302 | 4.0605 | 1 | 2.1354 | 0.5443 | 0.15273
Circuit No. 6 | 0 | 28.7867 | 0.46054 | 0.46054 | 28.7867 | 0.57082 | 0.57082 | 28.7867 | 0.81559 | 0.81559 | 28.7867 | 1.2455 | 1.2455 | 28.7867 | 2.1354 | 2.1354 | 29.7867 | 2.0302 | 2.0302
| 1 | 0.48151 | 0.001241 | 0.020969 | 0.60547 | 0.002453 | 0.032728 | 0.88382 | 0.007235 | 0.068231 | 1.4175 | 0.027673 | 0.16763 | 2.6797 | 0.15273 | 0.5443 | 2.0302 | 1 | 4.0605
| 2 | 0.48151 | 0.020969 | 0.001241 | 0.60547 | 0.032728 | 0.002453 | 0.88382 | 0.068231 | 0.007235 | 1.4175 | 0.16763 | 0.027673 | 2.6797 | 0.5443 | 0.15273 | 2.0302 | 4.0605 | 1
X Sequence/X1
|  | Circuit No. 1 |  |  | Circuit No. 2 |  |  | Circuit No. 3 |  |  | Circuit No. 4 |  |  | Circuit No. 5 |  |  | Circuit No. 6
|  | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 2
Circuit No. 1 | 0 | 14.9698 | 0.059031 | 0.059031 | 11.9074 | 0.20195 | 0.20195 | 10.4026 | 0.091257 | 0.091257 | 9.7128 | 0.063041 | 0.063041 | 9.3124 | 0.050913 | 0.050913 | 8.8995 | 0.040782 | 0.040782
| 1 | 0.059031 | 1 | 0.11806 | 0.21801 | 0.030266 | 0.015837 | 0.094368 | 0.00616 | 0.00311 | 0.064582 | 0.002926 | 0.001472 | 0.051867 | 0.001902 | 0.000954 | 0.041391 | 0.001217 | 0.00061
| 2 | 0.059031 | 0.11806 | 1 | 0.21801 | 0.015837 | 0.030266 | 0.094368 | 0.00311 | 0.00616 | 0.064582 | 0.001472 | 0.002926 | 0.051867 | 0.000954 | 0.001902 | 0.041391 | 0.00061 | 0.001217
Circuit No. 2 | 0 | 11.9074 | 0.21801 | 0.21801 | 14.9714 | 0.059454 | 0.059315 | 11.5236 | 0.16534 | 0.16534 | 10.4025 | 0.091153 | 0.091153 | 9.8452 | 0.067749 | 0.067749 | 9.3122 | 0.050907 | 0.050907
| 1 | 0.20195 | 0.030266 | 0.015837 | 0.059315 | 0.99919 | 0.1187 | 0.17564 | 0.020294 | 0.010478 | 0.094263 | 0.00614 | 0.00311 | 0.069374 | 0.003375 | 0.001699 | 0.051804 | 0.001898 | 0.000954
| 2 | 0.20195 | 0.015837 | 0.030266 | 0.059454 | 0.11884 | 0.99919 | 0.17564 | 0.010478 | 0.020294 | 0.094263 | 0.00311 | 0.00614 | 0.069374 | 0.001699 | 0.003375 | 0.051804 | 0.000954 | 0.001898
Circuit No. 3 | 0 | 10.4026 | 0.094368 | 0.094368 | 11.5236 | 0.17564 | 0.17564 | 14.9698 | 0.059031 | 0.059031 | 11.9074 | 0.20195 | 0.20195 | 10.8191 | 0.11391 | 0.11391 | 9.9879 | 0.073126 | 0.073126
| 1 | 0.091257 | 0.00616 | 0.00311 | 0.16534 | 0.020294 | 0.010478 | 0.059031 | 1 | 0.11806 | 0.21801 | 0.030266 | 0.015837 | 0.1188 | 0.009626 | 0.004886 | 0.07511 | 0.003943 | 0.001984
| 2 | 0.091257 | 0.00311 | 0.00616 | 0.16534 | 0.010478 | 0.020294 | 0.059031 | 0.11806 | 1 | 0.21801 | 0.015837 | 0.030266 | 0.1188 | 0.004886 | 0.009626 | 0.07511 | 0.001984 | 0.003943
Circuit No. 4 | 0 | 9.7128 | 0.064582 | 0.064582 | 10.4025 | 0.094263 | 0.094263 | 11.9074 | 0.21801 | 0.21801 | 14.9714 | 0.059384 | 0.059384 | 12.3961 | 0.2604 | 0.2604 | 10.8186 | 0.11388 | 0.11388
| 1 | 0.063041 | 0.002926 | 0.001472 | 0.091153 | 0.00614 | 0.00311 | 0.20195 | 0.030266 | 0.015837 | 0.059384 | 0.99919 | 0.11877 | 0.28674 | 0.049726 | 0.026618 | 0.11863 | 0.009606 | 0.004883
| 2 | 0.063041 | 0.001472 | 0.002926 | 0.091153 | 0.00311 | 0.00614 | 0.20195 | 0.015837 | 0.030266 | 0.059384 | 0.11877 | 0.99919 | 0.28674 | 0.026618 | 0.049726 | 0.11863 | 0.004883 | 0.009606
Circuit No. 5 | 0 | 9.3124 | 0.051867 | 0.051867 | 9.8452 | 0.069374 | 0.069374 | 10.8191 | 0.1188 | 0.1188 | 12.3961 | 0.28674 | 0.28674 | 14.9698 | 0.059031 | 0.059031 | 11.9066 | 0.20209 | 0.20209
| 1 | 0.050913 | 0.001902 | 0.000954 | 0.067749 | 0.003375 | 0.001699 | 0.11391 | 0.009626 | 0.004886 | 0.2604 | 0.049726 | 0.026618 | 0.059031 | 1 | 0.11806 | 0.21792 | 0.030294 | 0.015826
| 2 | 0.050913 | 0.000954 | 0.001902 | 0.067749 | 0.001699 | 0.003375 | 0.11391 | 0.004886 | 0.009626 | 0.2604 | 0.026618 | 0.049726 | 0.059031 | 0.11806 | 1 | 0.21792 | 0.015826 | 0.030294
Circuit No. 6 | 0 | 8.8995 | 0.041391 | 0.041391 | 9.3122 | 0.051804 | 0.051804 | 9.9879 | 0.07511 | 0.07511 | 10.8186 | 0.11863 | 0.11863 | 11.9066 | 0.21792 | 0.21792 | 14.9698 | 0.059031 | 0.059031
| 1 | 0.040782 | 0.001217 | 0.00061 | 0.050907 | 0.001898 | 0.000954 | 0.073126 | 0.003943 | 0.001984 | 0.11388 | 0.009606 | 0.004883 | 0.20209 | 0.030294 | 0.015826 | 0.059031 | 1 | 0.11806
| 2 | 0.040782 | 0.00061 | 0.001217 | 0.050907 | 0.000954 | 0.001898 | 0.073126 | 0.001984 | 0.003943 | 0.11388 | 0.004883 | 0.009606 | 0.20209 | 0.015826 | 0.030294 | 0.059031 | 0.11806 | 1
Symmetrical Components [Ω/mile]
Circuit | Z0 | Z1 | Z2 | ZOM(1,2) | ZOM(1,3) | ZOM(1,4) | ZOM(1,5) | ZOM(1,6) | ZOM(2,3) | ZOM(2,4) | ZOM(2,5) | ZOM(2,6) | ZOM(3,4) | ZOM(3,5) | ZOM(3,6) | ZOM(4,5) | ZOM(4,6) | ZOM(5,6)
1 | 0.295836 + j 2.952235 | Circuit No. 1 0: 0.009932 + j 0.197213; Circuit No. 1 1: 0.009932 + j 0.197213; Circuit No. 1 2: 0.285905 + j 2.348285; Circuit No. 2 0: 0.285905 + j 2.051516; Circuit No. 2 1: 0.285905 + j 1.915478; Circuit No. 2 2: 0.285905 + j 1.83652; Circuit No. 3 0: 0.285905 + j 1.755095
2 | 0.295821 + j 2.952554 | Circuit No. 1 0: 0.009916 + j 0.197053; Circuit No. 1 1: 0.009916 + j 0.197053; Circuit No. 1 2: 0.285905 + j 2.348285; Circuit No. 3 1: 0.285905 + j 2.272605; Circuit No. 3 2: 0.285905 + j 2.051508; Circuit No. 4 0: 0.285905 + j 1.941592; Circuit No. 4 1: 0.285905 + j 1.836475
3 | 0.295836 + j 2.952235 | Circuit No. 1 0: 0.009932 + j 0.197213; Circuit No. 1 1: 0.009932 + j 0.197213; Circuit No. 2 0: 0.285905 + j 2.051516; Circuit No. 3 1: 0.285905 + j 2.272605; Circuit No. 4 2: 0.285905 + j 2.348285; Circuit No. 5 0: 0.285905 + j 2.133667; Circuit No. 5 1: 0.285905 + j 1.969737
4 | 0.295836 + j 2.952554 | Circuit No. 1 0: 0.009932 + j 0.197053; Circuit No. 1 1: 0.009932 + j 0.197053; Circuit No. 2 1: 0.285905 + j 1.915478; Circuit No. 3 2: 0.285905 + j 2.051508; Circuit No. 4 2: 0.285905 + j 2.348285; Circuit No. 5 2: 0.285905 + j 2.444661; Circuit No. 6 0: 0.285905 + j 2.13356
5 | 0.295836 + j 2.952235 | Circuit No. 1 0: 0.009932 + j 0.197213; Circuit No. 1 1: 0.009932 + j 0.197213; Circuit No. 2 2: 0.285905 + j 1.83652; Circuit No. 4 0: 0.285905 + j 1.941592; Circuit No. 5 0: 0.285905 + j 2.133667; Circuit No. 5 2: 0.285905 + j 2.444661; Circuit No. 6 1: 0.285905 + j 2.348123
6 | 0.295836 + j 2.952235 | Circuit No. 1 0: 0.009932 + j 0.197213; Circuit No. 1 1: 0.009932 + j 0.197213; Circuit No. 3 0: 0.285905 + j 1.755095; Circuit No. 4 1: 0.285905 + j 1.836475; Circuit No. 5 1: 0.285905 + j 1.969737; Circuit No. 6 0: 0.285905 + j 2.13356; Circuit No. 6 1: 0.285905 + j 2.348123
Y Primitive [µS/mile]
Circuit No. 1 |  | Circuit No. 2 1: Circuit No. 2; Circuit No. 4 1: Circuit No. 3; Circuit No. 6 1: Circuit No. 4 |  |  |  |  | Circuit No. 5 | [5 empty] | Circuit No. 6
A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C | A | A | B | B | C | C
0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058 | 0.129408 + j 129.408058
Y Circuit [µS/mile] | bar: Circuit No. 1 0 to Circuit No. 6 0
Circuit No. 1 |  | Circuit No. 1 1: Circuit No. 2; Circuit No. 2 1: Circuit No. 3; Circuit No. 3 1: Circuit No. 4; Circuit No. 4 1: Circuit No. 5; Circuit No. 5 1: Circuit No. 6
A | B | C | A | B | C | A | B | C | A | B | C | A | B | C | A | B | C
0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116
Y Sequence [µS/mile] | bar: Circuit No. 1 0 to Circuit No. 6 0
Circuit No. 1 |  | Circuit No. 1 1: Circuit No. 2; Circuit No. 2 1: Circuit No. 3; Circuit No. 3 1: Circuit No. 4; Circuit No. 4 1: Circuit No. 5; Circuit No. 5 1: Circuit No. 6
0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 2 | 0 | 1 | 2
0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116 | 0.258816 + j 258.816116

## Electrical Parameters
Electrical Parameters
CYMCAP Version |  | 8.2 Revision 3
Study: |  | HOMER CITY GENERATION
Execution: |  | Three Units Deepest Depth 12 31
Date: |  | 1/8/2026 12:32:16 PM
No. | Description |  | Unit | Cable No.1 | Cable No.2 | Cable No.3 | Cable No.4 | Cable No.5 | Cable No.6 | Cable No.7 | Cable No.8 | Cable No.9 | Cable No.10 | Cable No.11 | Cable No.12 | Cable No.13 | Cable No.14 | Cable No.15 | Cable No.16 | Cable No.17 | Cable No.18 | Cable No.19 | Cable No.20 | Cable No.21 | Cable No.22 | Cable No.23 | Cable No.24 | Cable No.25 | Cable No.26 | Cable No.27 | Cable No.28 | Cable No.29 | Cable No.30 | Cable No.31 | Cable No.32 | Cable No.33 | Cable No.34 | Cable No.35 | Cable No.36
1 | Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY
Resistances
2 | DC Resistance of the conductor at 20°C |  | [Ω/mile] | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119
DC Resistance of the conductor at 20°C Equation
3 | DC Resistance of Conductor at Operating Temperature |  | [Ω/mile] | 0.013378 | 0.013181 | 0.013102 | 0.013286 | 0.013282 | 0.013011 | 0.013662 | 0.013761 | 0.01365 | 0.013758 | 0.013652 | 0.013552 | 0.013802 | 0.013886 | 0.013802 | 0.013896 | 0.013785 | 0.013713 | 0.01405 | 0.013966 | 0.014024 | 0.013936 | 0.014084 | 0.01392 | 0.013655 | 0.013763 | 0.013933 | 0.01375 | 0.013871 | 0.013825 | 0.01322 | 0.013411 | 0.013506 | 0.013317 | 0.013521 | 0.013606
DC Resistance of Conductor at Operating Temperature Equation
4 | AC Resistance of Conductor at 20°C |  | [Ω/mile] | 0.017572 | 0.017618 | 0.017572 | 0.017572 | 0.017618 | 0.017572 | 0.017572 | 0.017618 | 0.017572 | 0.017572 | 0.017618 | 0.017572 | 0.017572 | 0.017618 | 0.017572 | 0.017572 | 0.017618 | 0.017572 | 0.017572 | 0.017618 | 0.017572 | 0.017572 | 0.017618 | 0.017572 | 0.017572 | 0.017618 | 0.017572 | 0.017572 | 0.017618 | 0.017572 | 0.017572 | 0.017618 | 0.017572 | 0.017572 | 0.017618 | 0.017572
5 | AC Resistance of Conductor at Operating Temperature |  | [Ω/mile] | 0.019398 | 0.01928 | 0.019167 | 0.019321 | 0.019364 | 0.019091 | 0.019635 | 0.019765 | 0.019625 | 0.019715 | 0.019674 | 0.019543 | 0.019752 | 0.019869 | 0.019751 | 0.01983 | 0.019784 | 0.019677 | 0.019958 | 0.019935 | 0.019937 | 0.019864 | 0.020034 | 0.01985 | 0.019629 | 0.019766 | 0.019861 | 0.019708 | 0.019856 | 0.019771 | 0.019266 | 0.019472 | 0.019504 | 0.019347 | 0.019564 | 0.019588
AC Resistance of Conductor at Operating Temperature Equation
6 | DC Resistance of Sheath at 20°C |  | [Ω/mile] | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309 | 0.51309
7 | DC Resistance of Sheath at Operating Temperature |  | [Ω/mile] | 0.6107 | 0.60169 | 0.59804 | 0.60648 | 0.60629 | 0.59389 | 0.62281 | 0.62735 | 0.62226 | 0.6272 | 0.62237 | 0.61778 | 0.63013 | 0.63397 | 0.63011 | 0.63444 | 0.62933 | 0.62603 | 0.64054 | 0.63671 | 0.63937 | 0.63535 | 0.64212 | 0.63462 | 0.62339 | 0.62833 | 0.63609 | 0.62773 | 0.63325 | 0.63119 | 0.6026 | 0.6113 | 0.61565 | 0.60704 | 0.61635 | 0.62023
DC Resistance of Sheath at Operating Temperature Equation
8 | DC Resistance of Concentric Wires at 20°C |  | [Ω/mile] | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032 | 3.4032
9 | DC Resistance of Concentric Wires at Operating Temperature |  | [Ω/mile] | 4.0506 | 3.9909 | 3.9667 | 4.0226 | 4.0214 | 3.9391 | 4.1309 | 4.1611 | 4.1273 | 4.1601 | 4.128 | 4.0976 | 4.1795 | 4.205 | 4.1794 | 4.2081 | 4.1742 | 4.1523 | 4.2486 | 4.2232 | 4.2408 | 4.2142 | 4.259 | 4.2093 | 4.1348 | 4.1676 | 4.2191 | 4.1636 | 4.2002 | 4.1865 | 3.9969 | 4.0546 | 4.0835 | 4.0264 | 4.0881 | 4.1138
DC Resistance of Concentric Wires at Operating Temperature Equation
Losses
10 | Conductor Losses |  | [W/ft] | 0.54172 | 0.53844 | 0.53528 | 0.53957 | 0.54079 | 0.53317 | 0.88922 | 0.8951 | 0.88877 | 0.89285 | 0.89098 | 0.88507 | 0.55161 | 0.55488 | 0.55161 | 0.55381 | 0.55251 | 0.54953 | 0.90387 | 0.90283 | 0.90291 | 0.89959 | 0.9073 | 0.89898 | 0.54818 | 0.55201 | 0.55465 | 0.55039 | 0.55451 | 0.55215 | 0.87253 | 0.88183 | 0.88331 | 0.8762 | 0.886 | 0.88709
Conductor Losses Equation
11 | Dielectric Losses |  | [W/ft] | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151
Dielectric Losses Equation
12 | Metallic Screen Losses |  | [W/ft] | 0.02906 | 0.095402 | 0.033461 | 0.02926 | 0.09468 | 0.033694 | 0.049498 | 0.14917 | 0.048481 | 0.049153 | 0.15036 | 0.048832 | 0.026847 | 0.07729 | 0.027922 | 0.026665 | 0.077857 | 0.028102 | 0.04254 | 0.12773 | 0.044909 | 0.042885 | 0.12665 | 0.045243 | 0.02689 | 0.066436 | 0.026393 | 0.026705 | 0.065922 | 0.026597 | 0.055328 | 0.16096 | 0.049159 | 0.054926 | 0.15965 | 0.048798
Metallic Screen Losses Equation
13 | Armor/Pipe Losses |  | [W/ft] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Armor/Pipe Losses Equation
14 | Total Losses |  | [W/ft] | 1.5423 | 1.6054 | 1.5403 | 1.5403 | 1.607 | 1.5384 | 1.9102 | 2.0158 | 1.9088 | 1.9135 | 2.0129 | 1.9054 | 1.55 | 1.6037 | 1.551 | 1.552 | 1.6019 | 1.5491 | 1.9179 | 2.0021 | 1.9193 | 1.914 | 2.0055 | 1.9157 | 1.5466 | 1.59 | 1.5526 | 1.5486 | 1.5919 | 1.5503 | 1.8994 | 2.0143 | 1.904 | 1.9026 | 2.0172 | 1.9074
Total Losses Equation
Capacitance, Inductance, Impedance
15 | Capacitance |  | [µF/mile] | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279
Capacitance Equation
16 | Inductance of Conductor |  | [mH/mile] | 0.90225 | 0.86159 | 0.90225 | 0.90225 | 0.86159 | 0.90225 | 0.90225 | 0.86159 | 0.90225 | 0.90225 | 0.86159 | 0.90225 | 0.90225 | 0.86159 | 0.90225 | 0.90225 | 0.86159 | 0.90225 | 0.90225 | 0.86159 | 0.90225 | 0.90225 | 0.86159 | 0.90225 | 0.90225 | 0.86159 | 0.90225 | 0.90225 | 0.86159 | 0.90225 | 0.90225 | 0.86159 | 0.90225 | 0.90225 | 0.86159 | 0.90225
Inductance of Conductor Equation
17 | Reactance of Conductor |  | [Ω/mile] | 0.34014 | 0.32481 | 0.34014 | 0.34014 | 0.32481 | 0.34014 | 0.34014 | 0.32481 | 0.34014 | 0.34014 | 0.32481 | 0.34014 | 0.34014 | 0.32481 | 0.34014 | 0.34014 | 0.32481 | 0.34014 | 0.34014 | 0.32481 | 0.34014 | 0.34014 | 0.32481 | 0.34014 | 0.34014 | 0.32481 | 0.34014 | 0.34014 | 0.32481 | 0.34014 | 0.34014 | 0.32481 | 0.34014 | 0.34014 | 0.32481 | 0.34014
Reactance of Conductor Equation
18 | Inductance of Metallic Sheath |  | [mH/mile] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inductance of Metallic Sheath Equation
19 | Reactance of Metallic Sheath |  | [Ω/mile] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Reactance of Metallic Sheath Equation
20 | Positive Sequence Impedance |  | [Ω/mile] | 0.019398 + j0.340140 | 0.019280 + j0.324814 | 0.019167 + j0.340140 | 0.019321 + j0.340140 | 0.019364 + j0.324814 | 0.019091 + j0.340140 | 0.019635 + j0.340140 | 0.019765 + j0.324814 | 0.019625 + j0.340140 | 0.019715 + j0.340140 | 0.019674 + j0.324814 | 0.019543 + j0.340140 | 0.019752 + j0.340140 | 0.019869 + j0.324814 | 0.019751 + j0.340140 | 0.019830 + j0.340140 | 0.019784 + j0.324814 | 0.019677 + j0.340140 | 0.019958 + j0.340140 | 0.019935 + j0.324814 | 0.019937 + j0.340140 | 0.019864 + j0.340140 | 0.020034 + j0.324814 | 0.019850 + j0.340140 | 0.019629 + j0.340140 | 0.019766 + j0.324814 | 0.019861 + j0.340140 | 0.019708 + j0.340140 | 0.019856 + j0.324814 | 0.019771 + j0.340140 | 0.019266 + j0.340140 | 0.019472 + j0.324814 | 0.019504 + j0.340140 | 0.019347 + j0.340140 | 0.019564 + j0.324814 | 0.019588 + j0.340140
Positive Sequence Impedance Equation
21 | Negative Sequence Impedance |  | [Ω/mile] | 0.019398 + j0.340140 | 0.019280 + j0.324814 | 0.019167 + j0.340140 | 0.019321 + j0.340140 | 0.019364 + j0.324814 | 0.019091 + j0.340140 | 0.019635 + j0.340140 | 0.019765 + j0.324814 | 0.019625 + j0.340140 | 0.019715 + j0.340140 | 0.019674 + j0.324814 | 0.019543 + j0.340140 | 0.019752 + j0.340140 | 0.019869 + j0.324814 | 0.019751 + j0.340140 | 0.019830 + j0.340140 | 0.019784 + j0.324814 | 0.019677 + j0.340140 | 0.019958 + j0.340140 | 0.019935 + j0.324814 | 0.019937 + j0.340140 | 0.019864 + j0.340140 | 0.020034 + j0.324814 | 0.019850 + j0.340140 | 0.019629 + j0.340140 | 0.019766 + j0.324814 | 0.019861 + j0.340140 | 0.019708 + j0.340140 | 0.019856 + j0.324814 | 0.019771 + j0.340140 | 0.019266 + j0.340140 | 0.019472 + j0.324814 | 0.019504 + j0.340140 | 0.019347 + j0.340140 | 0.019564 + j0.324814 | 0.019588 + j0.340140
Negative Sequence Impedance Equation
22 | Zero Sequence Impedance |  | [Ω/mile] | 0.461956 + j0.122227 | 0.462057 + j0.122227 | 0.462099 + j0.122227 | 0.462003 + j0.122227 | 0.462005 + j0.122227 | 0.462147 + j0.122227 | 0.461816 + j0.122227 | 0.461768 + j0.122227 | 0.461821 + j0.122227 | 0.461770 + j0.122227 | 0.461820 + j0.122227 | 0.461869 + j0.122227 | 0.461749 + j0.122227 | 0.461709 + j0.122227 | 0.461749 + j0.122227 | 0.461704 + j0.122227 | 0.461757 + j0.122227 | 0.461791 + j0.122227 | 0.461633 + j0.122227 | 0.461672 + j0.122227 | 0.461645 + j0.122227 | 0.461686 + j0.122227 | 0.461618 + j0.122227 | 0.461693 + j0.122227 | 0.461819 + j0.122227 | 0.461767 + j0.122227 | 0.461687 + j0.122227 | 0.461773 + j0.122227 | 0.461716 + j0.122227 | 0.461738 + j0.122227 | 0.462037 + j0.122227 | 0.461940 + j0.122227 | 0.461892 + j0.122227 | 0.461987 + j0.122227 | 0.461885 + j0.122227 | 0.461843 + j0.122227
Zero Sequence Impedance Equation
23 | Surge Impedance |  | [Ω] | 51.2916 | 50.1227 | 51.2916 | 51.2916 | 50.1227 | 51.2916 | 51.2916 | 50.1227 | 51.2916 | 51.2916 | 50.1227 | 51.2916 | 51.2916 | 50.1227 | 51.2916 | 51.2916 | 50.1227 | 51.2916 | 51.2916 | 50.1227 | 51.2916 | 51.2916 | 50.1227 | 51.2916 | 51.2916 | 50.1227 | 51.2916 | 51.2916 | 50.1227 | 51.2916 | 51.2916 | 50.1227 | 51.2916 | 51.2916 | 50.1227 | 51.2916
Surge Impedance Equation
Others
24 | Dielectric Stress at Insulation Inner Surface |  | [kV/in] | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305 | 233.8305
Dielectric Stress at Insulation Inner Surface Equation
25 | Dielectric Stress at Insulation Outer Surface |  | [kV/in] | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566 | 121.8566
26 | Insulation Resistance at 60°F (15.8°C) |  | [㏁.1000ft] | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277 | 525.9277
Insulation Resistance at 60°F (15.8°C) Equation
27 | Reduction Factor (2pt bonded & single metallic screen) |  |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Reduction Factor Equation (2pt bonded & single metallic screen)
28 | Charging Current for One Cable (Phase) |  | [A/mile] | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528 | 25.7528
Charging Current Equation for One Cable (Phase)
29 | Charging Capacity of three phase system at Uo |  | [kvar/mile] | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691 | 15388.7691
Charging Capacity of three phase system at Uo Equation
30 | Voltage drop for Three Phase System |  | [V/A/mile] | 0.033598 | 0.033394 | 0.033198 | 0.033464 | 0.03354 | 0.033067 | 0.034008 | 0.034233 | 0.033991 | 0.034147 | 0.034076 | 0.033849 | 0.034211 | 0.034413 | 0.034211 | 0.034347 | 0.034267 | 0.034082 | 0.034569 | 0.034529 | 0.034532 | 0.034405 | 0.0347 | 0.034382 | 0.033998 | 0.034235 | 0.0344 | 0.034135 | 0.034391 | 0.034245 | 0.03337 | 0.033726 | 0.033782 | 0.03351 | 0.033885 | 0.033927
Voltage drop Equation for Three Phase System
31 | Induced Voltage (standing) on Sheath |  | [V/mile] | 24.5826 | 124.7403 | 204.2962 | 24.5927 | 124.7517 | 204.3023 | 103.3151 | 111.5703 | 176.0972 | 103.3177 | 111.5642 | 176.1047 | 72.6345 | 84.9115 | 130.1541 | 72.6353 | 84.9071 | 130.1591 | 124.4594 | 102.4351 | 135.3733 | 124.4558 | 102.4343 | 135.3799 | 151.1044 | 96.344 | 40.6889 | 151.1079 | 96.3327 | 40.6856 | 236.9844 | 140.8768 | 52.8351 | 236.99 | 140.8607 | 52.8351
32 | Induced Voltage angle on Sheath |  | [°] | -63.0803 | 138.6466 | -174.6498 | -63.1075 | 138.652 | -174.6538 | -14.3733 | 109.6488 | -171.4452 | -14.3618 | 109.6376 | -171.4516 | -19.1966 | 109.6542 | -170.0748 | -19.1841 | 109.6435 | -170.081 | -14.1672 | 92.1454 | -168.0028 | -14.1782 | 92.159 | -168.0117 | -9.3384 | 53.8249 | -136.9313 | -9.3325 | 53.8327 | -136.9555 | -5.6809 | 48.867 | -150.4336 | -5.676 | 48.8735 | -150.4105
33 | Induced Voltage (standing) on Concentric Wires |  | [V/mile] | 25.2925 | 125.2983 | 205.062 | 25.3025 | 125.3098 | 205.0682 | 104.3485 | 112.5811 | 177.096 | 104.351 | 112.575 | 177.1035 | 73.462 | 85.7053 | 130.9455 | 73.4629 | 85.7008 | 130.9505 | 125.4918 | 103.507 | 136.3938 | 125.4881 | 103.5062 | 136.4005 | 151.8928 | 97.0253 | 41.5099 | 151.8963 | 97.0139 | 41.5066 | 237.9622 | 141.6866 | 53.9077 | 237.9679 | 141.6703 | 53.9077
34 | Induced Voltage angle on Concentric Wires |  | [°] | -62.0385 | 138.3574 | -174.5517 | -62.0659 | 138.3629 | -174.5556 | -14.532 | 109.4653 | -171.3183 | -14.5205 | 109.4541 | -171.3247 | -19.3198 | 109.4649 | -169.9482 | -19.3072 | 109.4541 | -169.9545 | -14.3008 | 92.1231 | -167.8635 | -14.3118 | 92.1367 | -167.8724 | -9.4506 | 54.1184 | -137.194 | -9.4446 | 54.1263 | -137.2181 | -5.7873 | 49.1523 | -150.4251 | -5.7823 | 49.1589 | -150.4022
35 | Induced current on Metallic Screen |  | [A] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Induced current on Metallic Screen Equation

## Steady State
Cable Parameters under Normal Operation
CYMCAP Version |  | 8.2 Revision 3
Study: |  | HOMER CITY GENERATION
Execution: |  | Three Units Deepest Depth 12 31
Date: |  | 1/8/2026 12:32:16 PM
No. | Symbol | Description | Unit | Cable No.1 | Cable No.2 | Cable No.3 | Cable No.4 | Cable No.5 | Cable No.6 | Cable No.7 | Cable No.8 | Cable No.9 | Cable No.10 | Cable No.11 | Cable No.12 | Cable No.13 | Cable No.14 | Cable No.15 | Cable No.16 | Cable No.17 | Cable No.18 | Cable No.19 | Cable No.20 | Cable No.21 | Cable No.22 | Cable No.23 | Cable No.24 | Cable No.25 | Cable No.26 | Cable No.27 | Cable No.28 | Cable No.29 | Cable No.30 | Cable No.31 | Cable No.32 | Cable No.33 | Cable No.34 | Cable No.35 | Cable No.36
1 |  | Cable Equipment ID |  | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY | HOMER CITY 345KV 5000KCMIL JULY
Normal Operation IEC 60287-1-1
Conductor AC Resistance
2 | R₀ | DC Resistance of the conductor at 20°C | [Ω/mile] | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119 | 0.01119
DC Resistance of the conductor at 20°C Equation
3 | R' | DC Resistance of Conductor at Operating Temperature | [Ω/mile] | 0.013378 | 0.013181 | 0.013102 | 0.013286 | 0.013282 | 0.013011 | 0.013662 | 0.013761 | 0.01365 | 0.013758 | 0.013652 | 0.013552 | 0.013802 | 0.013886 | 0.013802 | 0.013896 | 0.013785 | 0.013713 | 0.01405 | 0.013966 | 0.014024 | 0.013936 | 0.014084 | 0.01392 | 0.013655 | 0.013763 | 0.013933 | 0.01375 | 0.013871 | 0.013825 | 0.01322 | 0.013411 | 0.013506 | 0.013317 | 0.013521 | 0.013606
DC Resistance of Conductor at Operating Temperature Equation
4 | dc | Conductor Diameter | [in] | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48
5 | s | Distance Between Conductor Axes | [in] | 15.9311 | 14.0407 | 15.9311 | 15.9311 | 14.0407 | 15.9311 | 15.9311 | 14.0407 | 15.9311 | 15.9311 | 14.0407 | 15.9311 | 15.9311 | 14.0407 | 15.9311 | 15.9311 | 14.0407 | 15.9311 | 15.9311 | 14.0407 | 15.9311 | 15.9311 | 14.0407 | 15.9311 | 15.9311 | 14.0407 | 15.9311 | 15.9311 | 14.0407 | 15.9311 | 15.9311 | 14.0407 | 15.9311 | 15.9311 | 14.0407 | 15.9311
6 | ks | Factor Used for xs Calculation (Skin Effect) |  | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62
7 | kp | Factor Used for xp Calculation (Proximity Effect) |  | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37
8 | Xs² | Component of Ys Calculation (Skin Effect) |  | 11.2472 | 11.415 | 11.4844 | 11.3252 | 11.3286 | 11.5645 | 11.0133 | 10.9337 | 11.0229 | 10.9365 | 11.021 | 11.1026 | 10.9014 | 10.8355 | 10.9017 | 10.8275 | 10.9152 | 10.9725 | 10.7095 | 10.7736 | 10.7289 | 10.7966 | 10.6832 | 10.8089 | 11.0188 | 10.9325 | 10.7994 | 10.9429 | 10.8477 | 10.8832 | 11.3812 | 11.2198 | 11.1409 | 11.2982 | 11.1282 | 11.059
Component of Ys Calculation (Skin Effect) Equation
9 | Xp² | Component of Yp Calculation (Proximity Effect) |  | 6.712 | 6.8122 | 6.8536 | 6.7586 | 6.7606 | 6.9014 | 6.5725 | 6.5249 | 6.5782 | 6.5266 | 6.577 | 6.6257 | 6.5057 | 6.4664 | 6.5058 | 6.4616 | 6.5139 | 6.5481 | 6.3911 | 6.4294 | 6.4028 | 6.4431 | 6.3755 | 6.4505 | 6.5758 | 6.5242 | 6.4448 | 6.5304 | 6.4736 | 6.4948 | 6.792 | 6.6957 | 6.6486 | 6.7425 | 6.641 | 6.5997
Component of Yp Calculation (Proximity Effect) Equation
10 | ys | Skin Effect Factor |  | 0.43786 | 0.44686 | 0.45059 | 0.44204 | 0.44222 | 0.45489 | 0.42531 | 0.42104 | 0.42582 | 0.42119 | 0.42572 | 0.4301 | 0.41931 | 0.41578 | 0.41932 | 0.41535 | 0.42005 | 0.42312 | 0.40902 | 0.41245 | 0.41006 | 0.41369 | 0.40761 | 0.41435 | 0.42561 | 0.42097 | 0.41384 | 0.42153 | 0.41643 | 0.41833 | 0.44505 | 0.43639 | 0.43215 | 0.4406 | 0.43147 | 0.42776
Skin Effect Factor Equation
11 | yp | Proximity Effect Factor |  | 0.012119 | 0.01584 | 0.012365 | 0.0122 | 0.015725 | 0.012447 | 0.01187 | 0.015184 | 0.011881 | 0.011788 | 0.015305 | 0.011966 | 0.01175 | 0.015047 | 0.01175 | 0.011669 | 0.015158 | 0.011827 | 0.01154 | 0.014959 | 0.011561 | 0.011636 | 0.014831 | 0.011649 | 0.011876 | 0.015182 | 0.011639 | 0.011795 | 0.015064 | 0.01173 | 0.012258 | 0.015578 | 0.012006 | 0.012172 | 0.015453 | 0.011919
Proximity Effect Factor Equation
12 | R | AC Resistance of Conductor at Operating Temperature | [Ω/mile] | 0.019398 | 0.01928 | 0.019167 | 0.019321 | 0.019364 | 0.019091 | 0.019635 | 0.019765 | 0.019625 | 0.019715 | 0.019674 | 0.019543 | 0.019752 | 0.019869 | 0.019751 | 0.01983 | 0.019784 | 0.019677 | 0.019958 | 0.019935 | 0.019937 | 0.019864 | 0.020034 | 0.01985 | 0.019629 | 0.019766 | 0.019861 | 0.019708 | 0.019856 | 0.019771 | 0.019266 | 0.019472 | 0.019504 | 0.019347 | 0.019564 | 0.019588
AC Resistance of Conductor at Operating Temperature Equation
Dielectric Losses
13 | tanδ | Dielectric Loss Factor |  | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001
14 | ε | Insulation Relative Permittivity |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
15 | C | Cable Capacitance | [µF/mile] | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279 | 0.34279
Cable Capacitance Equation
16 | U₀ | Voltage | [kV] | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858 | 199.1858
17 | Wd | Cable Dielectric Losses Per Phase | [W/ft] | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151 | 0.97151
Cable Dielectric Losses Per Phase Equation
Filament method
18 | ƛ'₁ | Screen Loss Factor Caused by Circulating Current |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | ƛ''₁ | Screen Loss Factor Caused by Eddy Current |  | 0.053643 | 0.17718 | 0.06251 | 0.054229 | 0.17508 | 0.063195 | 0.055664 | 0.16665 | 0.054549 | 0.055052 | 0.16876 | 0.055173 | 0.04867 | 0.13929 | 0.050619 | 0.048148 | 0.14091 | 0.051139 | 0.047065 | 0.14147 | 0.049739 | 0.047672 | 0.13959 | 0.050327 | 0.049053 | 0.12035 | 0.047585 | 0.048519 | 0.11888 | 0.04817 | 0.063411 | 0.18253 | 0.055654 | 0.062687 | 0.18019 | 0.055009
20 | ƛ₁ | Screen Loss Factor |  | 0.053643 | 0.17718 | 0.06251 | 0.054229 | 0.17508 | 0.063195 | 0.055664 | 0.16665 | 0.054549 | 0.055052 | 0.16876 | 0.055173 | 0.04867 | 0.13929 | 0.050619 | 0.048148 | 0.14091 | 0.051139 | 0.047065 | 0.14147 | 0.049739 | 0.047672 | 0.13959 | 0.050327 | 0.049053 | 0.12035 | 0.047585 | 0.048519 | 0.11888 | 0.04817 | 0.063411 | 0.18253 | 0.055654 | 0.062687 | 0.18019 | 0.055009
21 | ƛ₂a | Armour Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | ƛ₂pipe | Pipe Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | ƛ₂ | Armour Loss Factor + Pipe Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Armour Loss Factor + Pipe Loss Factor Equation
Normal Operation IEC 60287-2-1
24 | T₁ | Thermal Resistance Between Conductor and Screen | [K.m/W] | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868 | 0.39868
Thermal Resistance Between Conductor and Screen Equation
25 | t₁ | Insulation Thickness Between Conductor and Screen | [in] | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335 | 1.335
26 | ρTi | Thermal Resistivity of Insulation | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
27 | T₃ | Thermal Resistance of Jacket/Pipe Coating | [K.m/W] | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863 | 0.067863
Thermal Resistance of Jacket/Pipe Coating Equation
28 | t₃ | Thickness of Jacket/Pipe Coating | [in] | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346
29 | ρTJ | Thermal Resistivity of Jacket/Pipe Coating | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
30 | T Conductor Shield | Thermal resistance | [K.m/W]
31 |  | Thermal resistance equation
32 |  | Thermal resistivity | [K.m/W] | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
33 |  | Layer thickness | [in] | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067
34 |  | Internal diameter | [in] | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48
35 | T Insulation | Thermal resistance | [K.m/W]
36 |  | Thermal resistance equation
37 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
38 |  | Layer thickness | [in] | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201 | 1.201
39 |  | Internal diameter | [in] | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614
40 | T Insulation Screen | Thermal resistance | [K.m/W]
41 |  | Thermal resistance equation
42 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
43 |  | Layer thickness | [in] | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067
44 |  | Internal diameter | [in] | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016
45 | T Concentric wires | Thermal resistance | [K.m/W]
46 |  | Thermal resistance equation
47 |  | Thermal resistivity | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 |  | Layer thickness | [in] | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906 | 0.0906
49 |  | Internal diameter | [in] | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15
50 | T Sheath | Thermal resistance | [K.m/W]
51 |  | Thermal resistance equation
52 |  | Thermal resistivity | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 |  | Layer thickness | [in] | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001 | 0.0050001
54 |  | Internal diameter | [in] | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312
55 | T Jacket | Thermal resistance | [K.m/W]
56 |  | Thermal resistance equation
57 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
58 |  | Layer thickness | [in] | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346 | 0.346
59 |  | Internal diameter | [in] | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412
Thermal resistance inside the duct
60 | U | Constant from IEC6028721 clause4272 |  | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87
61 | V | Constant from IEC6028721 clause4272 |  | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312
62 | Y | Constant from IEC6028721 clause4272 |  | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037
63 | θm | Mean temperature of the medium in conduit | [°C] | 67.5702 | 63.0558 | 61.2781 | 65.4725 | 65.3447 | 59.2126 | 73.3975 | 75.604 | 73.1279 | 75.5806 | 73.1238 | 70.8983 | 77.2295 | 79.1106 | 77.2209 | 79.3737 | 76.8033 | 75.1929 | 82.2163 | 80.2672 | 81.6353 | 79.6385 | 82.9545 | 79.2746 | 73.882 | 76.3143 | 80.1952 | 76.0391 | 78.7613 | 77.7565 | 63.3479 | 67.6138 | 69.8398 | 65.5564 | 70.1248 | 72.1151
64 | Deq | Equivalent diameter of the cables inside the conduit | [in] | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332
65 | T₄' | Thermal resistance of the medium in conduit | [K.m/W] | 0.19454 | 0.19986 | 0.20204 | 0.19698 | 0.19713 | 0.20463 | 0.18808 | 0.18574 | 0.18836 | 0.18576 | 0.18837 | 0.19079 | 0.18405 | 0.18214 | 0.18406 | 0.18188 | 0.18449 | 0.18617 | 0.17907 | 0.18099 | 0.17964 | 0.18161 | 0.17835 | 0.18198 | 0.18756 | 0.185 | 0.18106 | 0.18528 | 0.18249 | 0.18351 | 0.19951 | 0.19449 | 0.19197 | 0.19688 | 0.19165 | 0.18946
Thermal resistance of the medium in conduit Equation
Thermal resistance of the duct
66 | Do | Outer diameter of the conduit | [in] | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625
67 | Di | Inner diameter of the conduit | [in] | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981 | 7.981
68 | ρT | Thermal resistivity of the conduit material | [K.m/W] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
69 | T₄'' | Thermal resistance of the conduit | [K.m/W] | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104 | 0.074104
Thermal resistance of the conduit Equation
Thermal resistance of the external medium
70 | L | Depth of cable/conduit axis | [ft] | 6.8279 | 5.8279 | 6.8279 | 5.8279 | 6.8279 | 5.8279 | 5.8279 | 6.8279 | 6.8279 | 6.8279 | 5.8279 | 5.8279 | 5.8279 | 6.8279 | 6.8279 | 6.8279 | 5.8279 | 5.8279 | 6.8279 | 5.8279 | 6.8279 | 5.8279 | 6.8279 | 5.8279 | 5.8279 | 5.8279 | 6.8279 | 6.8279 | 6.8279 | 5.8279 | 5.8279 | 5.8279 | 5.8279 | 6.8279 | 6.8279 | 6.8279
71 | De / Do | External diameter of the cable conduit | [ft] | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875
72 | u | Geometric factor as per IEC60287-2-1 clause 4.2.2 |  | 18.9994 | 16.2168 | 18.9994 | 16.2168 | 18.9994 | 16.2168 | 16.2168 | 18.9994 | 18.9994 | 18.9994 | 16.2168 | 16.2168 | 16.2168 | 18.9994 | 18.9994 | 18.9994 | 16.2168 | 16.2168 | 18.9994 | 16.2168 | 18.9994 | 16.2168 | 18.9994 | 16.2168 | 16.2168 | 16.2168 | 18.9994 | 18.9994 | 18.9994 | 16.2168 | 16.2168 | 16.2168 | 16.2168 | 18.9994 | 18.9994 | 18.9994
Geometric factor Equation as per IEC60287-2-1 clause 4.2.2
73 | ρTs | Thermal resistivity of the soil | [K.m/W] | 1.2001 | 1.1852 | 1.2083 | 1.1699 | 1.2218 | 1.1708 | 1.1783 | 1.2269 | 1.2041 | 1.2037 | 1.1974 | 1.1774 | 1.1903 | 1.2352 | 1.2086 | 1.2164 | 1.2061 | 1.1834 | 1.2337 | 1.2142 | 1.2199 | 1.2038 | 1.2449 | 1.1935 | 1.1842 | 1.2085 | 1.2317 | 1.2114 | 1.2394 | 1.2015 | 1.1646 | 1.186 | 1.1731 | 1.1987 | 1.2204 | 1.2019
74 | T₄'''self | Thermal resistance of the cable isolated | [K.m/W] | 0.69466 | 0.65609 | 0.69941 | 0.64765 | 0.70722 | 0.64813 | 0.65229 | 0.71015 | 0.69698 | 0.69673 | 0.66286 | 0.65179 | 0.65894 | 0.71497 | 0.69955 | 0.7041 | 0.66767 | 0.6551 | 0.7141 | 0.67214 | 0.70613 | 0.66638 | 0.72055 | 0.66069 | 0.65557 | 0.669 | 0.71295 | 0.70119 | 0.71739 | 0.66514 | 0.64472 | 0.65653 | 0.64938 | 0.69383 | 0.70637 | 0.6957
Thermal resistance of the cable isolated Equation
75 | T₄'''mutual | Thermal resistance associated to the temperature rise due to surrounding heat sources | [K.m/W] | 8.6545 | 7.4577 | 7.4132 | 8.2972 | 7.8335 | 7.0641 | 7.7964 | 7.618 | 7.7151 | 8.0861 | 7.3013 | 7.4175 | 10.5482 | 10.467 | 10.498 | 10.9106 | 10.087 | 10.1563 | 9.1061 | 8.4265 | 9.0141 | 8.7626 | 8.7715 | 8.7014 | 9.9148 | 10.0743 | 11.0591 | 10.2809 | 10.4819 | 10.6438 | 6.2347 | 6.4656 | 7.2561 | 6.5286 | 6.7858 | 7.5601
Thermal resistance associated to the temperature rise due to surrounding heat sources Equation
76 | Δθint | Temperature rise due to surrounding heat sources | [°C] | 43.792 | 39.279 | 37.4615 | 41.9309 | 41.3003 | 35.6535 | 48.8612 | 50.3812 | 48.3149 | 50.7638 | 48.2169 | 46.3696 | 53.64 | 55.0711 | 53.4216 | 55.5547 | 53.0126 | 51.6191 | 57.299 | 55.3494 | 56.7622 | 55.0243 | 57.7129 | 54.6901 | 50.309 | 52.5515 | 56.3316 | 52.2349 | 54.746 | 54.136 | 38.8514 | 42.7287 | 45.3262 | 40.7531 | 44.9082 | 47.3104
Temperature rise due to surrounding heat sources Equation
77 | T₄''' | Thermal resistance of the external medium | [K.m/W] | 9.3492 | 8.1138 | 8.1126 | 8.9448 | 8.5407 | 7.7122 | 8.4487 | 8.3281 | 8.4121 | 8.7828 | 7.9642 | 8.0693 | 11.2072 | 11.1819 | 11.1976 | 11.6147 | 10.7547 | 10.8114 | 9.8202 | 9.0987 | 9.7203 | 9.4289 | 9.492 | 9.362 | 10.5704 | 10.7433 | 11.772 | 10.9821 | 11.1993 | 11.3089 | 6.8794 | 7.1221 | 7.9055 | 7.2224 | 7.4922 | 8.2558
Thermal resistance of the external medium Equation
Thermal Capacitance IEC 853-2
78 | Q Conductor | Thermal capacitance | [J/m.K]
79 |  | Thermal capacitance equation
80 |  | Material surface | [in²] | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202 | 3.9202
81 |  | Volumetric specific heat of the material | [J/(K*m³)] | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000
82 | Q Conductor Shield | Thermal capacitance | [J/m.K]
83 |  | Thermal capacitance equation
84 |  | External diameter | [in] | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614
85 |  | Internal diameter | [in] | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48
86 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
87 | Q1 Insulation | Thermal capacitance | [J/m.K]
88 |  | Thermal capacitance equation
89 |  | External diameter | [in] | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016
90 |  | Internal diameter | [in] | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614
91 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
92 | Q2 Insulation | Thermal capacitance | [J/m.K]
93 |  | Thermal capacitance equation
94 |  | External diameter | [in] | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016
95 |  | Internal diameter | [in] | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614
96 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
97 | Q Insulation Screen | Thermal capacitance | [J/m.K]
98 |  | Thermal capacitance equation
99 |  | External diameter | [in] | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15
100 |  | Internal diameter | [in] | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016 | 5.016
101 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
102 | Q Concentric wires | Thermal capacitance | [J/m.K]
103 |  | Thermal capacitance equation
104 |  | Number of armour wires |  | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
105 |  | Mean diameter of armour wire | [in] | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598 | 0.090598
106 |  | Length of lay | [in] | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937 | 0.3937
107 |  | Mean diameter of armour | [in] | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406 | 5.2406
108 |  | Wire Shape is half-circle |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | Q Sheath | Thermal capacitance | [J/m.K]
110 |  | Thermal capacitance equation
111 |  | External diameter | [in] | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412
112 |  | Internal diameter | [in] | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312 | 5.3312
113 |  | Volumetric specific heat of the material | [J/(K*m³)] | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000
114 | Q Jacket | Thermal capacitance | [J/m.K]
115 |  | Thermal capacitance equation
116 |  | External diameter | [in] | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332 | 6.0332
117 |  | Internal diameter | [in] | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412
118 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
Ampacity
119 | T₄ | Total external thermal resistance | [K.m/W] | 9.6178 | 8.3877 | 8.3888 | 9.2159 | 8.812 | 7.9909 | 8.7109 | 8.588 | 8.6746 | 9.0427 | 8.2266 | 8.3342 | 11.4653 | 11.4382 | 11.4558 | 11.8706 | 11.0133 | 11.0716 | 10.0733 | 9.3538 | 9.974 | 9.6847 | 9.7445 | 9.6181 | 10.8321 | 11.0024 | 12.0272 | 11.2415 | 11.4559 | 11.5665 | 7.153 | 7.3907 | 8.1715 | 7.4934 | 7.7579 | 8.5194
Total external thermal resistance Equation
120 | I | Cable core ampacity | [A] | 384 | 384 | 384 | 384 | 384 | 384 | 489 | 489 | 489 | 489 | 489 | 489 | 384 | 384 | 384 | 384 | 384 | 384 | 489 | 489 | 489 | 489 | 489 | 489 | 384 | 384 | 384 | 384 | 384 | 384 | 489 | 489 | 489 | 489 | 489 | 489
Cable core ampacity Equation

## Short Circuit
Cable Short Circuit
CYMCAP Version |  | 8.2 Revision 3
Study: |  | HOMER CITY GENERATION
Execution: |  | Three Units Deepest Depth 12 31
Date: |  | 1/8/2026 12:32:16 PM
Symbol | Description |  | Unit | Circuit No. 2
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | B | B | B
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 75.9948 | 74.1938 | 74.1938
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1203912.2718 | 18083.8646 | 114047.1211
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1205768.8854 | 22486.1275 | 115649.1718
Symbol | Description |  | Unit | Circuit No. 4
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | A | A | A
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 82.4468 | 80.6348 | 80.6348
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1175757.9635 | 17212.5557 | 108552.1523
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1177571.1589 | 21402.7106 | 110077.0137
Symbol | Description |  | Unit | Circuit No. 6
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | C | C | C
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 72.6541 | 70.8634 | 70.8634
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1218459.486 | 18525.141 | 116830.0605
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1220338.5335 | 23034.8264 | 118471.2039
Symbol | Description |  | Unit | Circuit No. 1
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | A | A | A
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 69.7497 | 68.4058 | 68.4058
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1231094.1071 | 18847.1469 | 118860.8127
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1232992.6392 | 23435.2201 | 120530.4827
Symbol | Description |  | Unit | Circuit No. 2
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | C | C | C
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 73.7119 | 71.9189 | 71.9189
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1213854.8259 | 18385.9125 | 115952.0064
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1215726.7724 | 22861.7046 | 117580.8156
Symbol | Description |  | Unit | Circuit No. 4
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | B | B | B
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 85.81 | 83.9877 | 83.9877
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1161043.8698 | 16748.4619 | 105625.3129
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1162834.3738 | 20825.6397 | 107109.0602
Symbol | Description |  | Unit | Circuit No. 6
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | A | A | A
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 68.3759 | 66.5945 | 66.5945
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1237066.9846 | 19082.6322 | 120345.9168
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1238974.7277 | 23728.031 | 122036.4484
Symbol | Description |  | Unit | Circuit No. 1
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | B | B | B
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 65.2792 | 63.9396 | 63.9396
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1250524.964 | 19425.1644 | 122506.1195
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1252453.4613 | 24153.9479 | 124226.9961
Symbol | Description |  | Unit | Circuit No. 3
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | A | A | A
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 79.3995 | 78.0426 | 78.0426
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1189066.4186 | 17566.2433 | 110782.7073
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1190900.1377 | 21842.4986 | 112338.902
Symbol | Description |  | Unit | Circuit No. 4
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | C | C | C
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 82.0843 | 80.273 | 80.273
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1177342.5954 | 17262.1799 | 108865.1108
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1179158.2346 | 21464.4152 | 110394.3684
Symbol | Description |  | Unit | Circuit No. 6
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | B | B | B
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 73.0024 | 71.208 | 71.208
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1216943.2939 | 18479.7425 | 116543.7517
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1218820.0033 | 22978.3762 | 118180.8733
Symbol | Description |  | Unit | Circuit No. 1
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | C | C | C
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 63.4671 | 62.1316 | 62.1316
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1258397.5243 | 19656.7202 | 123966.4418
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1260338.1623 | 24441.8727 | 125707.832
Symbol | Description |  | Unit | Circuit No. 3
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | B | B | B
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 81.308 | 79.9468 | 79.9468
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1180734.1755 | 17306.849 | 109146.8191
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1182555.0449 | 21519.9583 | 110680.034
Symbol | Description |  | Unit | Circuit No. 5
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | A | A | A
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 76.0546 | 74.7023 | 74.7023
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1203651.4595 | 18015.9717 | 113618.9498
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1205507.6708 | 22401.707 | 115214.9859
Symbol | Description |  | Unit | Circuit No. 6
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | C | C | C
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 74.9282 | 73.1326 | 73.1326
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1208558.3954 | 18225.1127 | 114937.9115
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1210422.174 | 22661.7604 | 116552.4754
Symbol | Description |  | Unit | Circuit No. 1
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | A | A | A
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 67.6543 | 66.3132 | 66.3132
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1240203.8899 | 19119.078 | 120575.7644
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1242116.4706 | 23773.349 | 122269.5248
Symbol | Description |  | Unit | Circuit No. 3
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | C | C | C
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 79.3915 | 78.0347 | 78.0347
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1189101.2598 | 17567.3249 | 110789.5281
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1190935.0326 | 21843.8434 | 112345.8186
Symbol | Description |  | Unit | Circuit No. 5
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | B | B | B
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 78.5083 | 77.1509 | 77.1509
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1192954.6106 | 17686.9457 | 111543.9251
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1194794.3258 | 21992.5842 | 113110.8128
Symbol | Description |  | Unit | Circuit No. 1
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | B | B | B
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 67.5649 | 66.2222 | 66.2222
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1240592.3508 | 19130.8575 | 120650.0526
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1242505.5305 | 23787.996 | 122344.8565
Symbol | Description |  | Unit | Circuit No. 3
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | A | A | A
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 81.542 | 80.1823 | 80.1823
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1179711.725 | 17274.6095 | 108943.4987
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1181531.0177 | 21479.8706 | 110473.8575
Symbol | Description |  | Unit | Circuit No. 5
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | C | C | C
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 82.3629 | 81.0021 | 81.0021
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1176124.82 | 17162.0943 | 108233.9141
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1177938.5812 | 21339.9651 | 109754.3051
Symbol | Description |  | Unit | Circuit No. 1
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | C | C | C
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 61.4043 | 60.0716 | 60.0716
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1267357.1871 | 19918.9644 | 125620.3028
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1269311.6423 | 24767.9566 | 127384.9251
Symbol | Description |  | Unit | Circuit No. 3
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | B | B | B
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 79.0028 | 77.6448 | 77.6448
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1190797.132 | 17620.1552 | 111122.706
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1192633.5201 | 21909.5345 | 112683.6767
Symbol | Description |  | Unit | Circuit No. 5
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | A | A | A
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 78.2098 | 76.8546 | 76.8546
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1194256.1749 | 17726.9443 | 111796.1788
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1196097.8973 | 22042.3199 | 113366.6099
Symbol | Description |  | Unit | Circuit No. 2
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | A | A | A
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 76.2106 | 74.4122 | 74.4122
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1202971.7585 | 18054.7271 | 113863.3633
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1204826.9217 | 22449.8968 | 115462.8328
Symbol | Description |  | Unit | Circuit No. 3
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | C | C | C
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 77.365 | 76.0109 | 76.0109
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1197939.9363 | 17840.555 | 112512.6726
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1199787.3396 | 22183.5876 | 114093.1685
Symbol | Description |  | Unit | Circuit No. 5
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | B | B | B
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 80.953 | 79.5924 | 79.5924
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1182284.2756 | 17355.3024 | 109452.3941
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1184107.5356 | 21580.207 | 110989.9015
Symbol | Description |  | Unit | Circuit No. 2
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | B | B | B
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 78.4733 | 76.6669 | 76.6669
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1193107.2835 | 17752.2565 | 111955.812
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1194947.2341 | 22073.794 | 113528.4855
Symbol | Description |  | Unit | Circuit No. 4
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | A | A | A
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 85.0243 | 83.2067 | 83.2067
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1164484.1405 | 16857.2691 | 106311.5132
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1166279.95 | 20960.9345 | 107804.8997
Symbol | Description |  | Unit | Circuit No. 5
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | C | C | C
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 79.9259 | 78.5684 | 78.5684
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1186768.7066 | 17494.849 | 110332.4539
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1188598.8822 | 21753.7242 | 111882.3237
Symbol | Description |  | Unit | Circuit No. 2
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | C | C | C
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 75.9406 | 74.1427 | 74.1427
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1204148.4564 | 18090.6824 | 114090.1176
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1206005.4343 | 22494.6049 | 115692.7723
Symbol | Description |  | Unit | Circuit No. 4
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | B | B | B
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 83.1238 | 81.3073 | 81.3073
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1172798.7114 | 17120.0884 | 107969.0008
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1174607.3432 | 21287.7334 | 109485.6706
Symbol | Description |  | Unit | Circuit No. 6
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | A | A | A
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 66.169 | 64.3924 | 64.3924
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1246658.6242 | 19366.9513 | 122138.9941
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1248581.159 | 24081.5635 | 123854.7136
Symbol | Description |  | Unit | Circuit No. 2
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | A | A | A
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 78.3929 | 76.5897 | 76.5897
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1193457.8011 | 17762.6614 | 112021.4308
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1195298.2923 | 22086.7318 | 113595.0262
Symbol | Description |  | Unit | Circuit No. 4
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | C | C | C
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 84.4446 | 82.6282 | 82.6282
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1167021.3256 | 16937.5757 | 106817.9719
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1168821.0478 | 21060.7906 | 108318.4729
Symbol | Description |  | Unit | Circuit No. 6
| Cable Equipment ID |  |  | HOMER CITY 345KV 5000KCMIL JULY
|  |  |  | Conductor | Sheath | Concentric neutral/Skid wires
|  |  |  | B | B | B
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483
S | Layer Cross-Sectional Area |  | [mm²] | 2529.184 | 54.0778 | 341.0456
θi | Initial Temperature |  | [°C] | 70.4938 | 68.7049 | 68.7049
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529
θf | Final Temperature |  | [°C] | 250 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 1227857.8827 | 18808.1114 | 118614.6329
Inad | Non Adiabatic Short Circuit Current |  | [A] | 1229751.424 | 23386.682 | 120280.8447